## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | Silica
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2013-04-01 | 7.59 | 121 | 0.2 | 2390 | 1618 | 1102 | 672 | 430 | 146 | 6.5 | 120 | NIL | 0.2 | 240 | 893 | 95
2013-04-02 | 7.86 | 118 | 0.2 | 2190 | 1479 | 918 | 560 | 358 | 125 | 7.2 | 150 | NIL | 0.2 | 236 | 984 | 91
2013-04-03 | 7.92 | 104 | 0.2 | 2100 | 1420 | 898 | 530 | 368 | 132 | 6.8 | 160 | NIL | 0.2 | 208 | 916 | 98
2013-04-04 | 7.98 | 85 | 0.2 | 2180 | 1470 | 877 | 510 | 367 | 125 | 8 | 165 | NIL | 0.2 | 170 | 966 | 110
2013-04-05 | 7.9 | 77 | 0.2 | 2150 | 1450 | 816 | 449 | 367 | 114 | 7.1 | 160 | NIL | 0.2 | 154 | 952 | 113
2013-04-06 | 7.8 | 62 | 0.2 | 2010 | 1360 | 775 | 428 | 347 | 110 | 7 | 150 | NIL | 0.2 | 120 | 938 | 108
2013-04-07 | 8.02 | 50 | 0.2 | 2000 | 1353 | 672 | 401 | 271 | 103 | 7 | 170 | NIL | 0.2 | 98 | 942 | 110
2013-04-08 | 8 | 49 | 0.2 | 1995 | 1348 | 726 | 416 | 310 | 114 | 7 | 170 | NIL | 0.2 | 90 | 956 | 112
2013-04-09 | 7.9 | 41 | 0.2 | 2050 | 1431 | 747 | 428 | 319 | 117 | 6.9 | 160 | NIL | 0.2 | 80 | 943 | 110
2013-04-10 | 7.88 | 52 | 0.1 | 2215 | 1550 | 726 | 420 | 306 | 114 | 6.8 | 160 | NIL | 0.2 | 101 | 929 | 108
2013-04-11 | 8.09 | 45 | 0.2 | 1740 | 1218 | 734 | 428 | 306 | 117 | 7 | 170 | NIL | 0.2 | 88 | 910 | 110
2013-04-12 | 7.98 | 37 | 0.2 | 1795 | 1256 | 747 | 428 | 319 | 125 | 6.8 | 170 | NIL | 0.2 | 74 | 925 | 108
2013-04-13 | 8.12 | 38 | 0.2 | 1968 | 1378 | 804 | 469 | 335 | 132 | 7.1 | 180 | NIL | 0.2 | 60 | 938 | 112
2013-04-14 | 7.94 | 22 | 0.2 | 2110 | 1477 | 849 | 510 | 339 | 189 | 7.1 | 165 | NIL | 0.2 | 48 | 949 | 110
2013-04-15 | 7.98 | 23 | 0.2 | 2128 | 1490 | 856 | 518 | 338 | 196 | 7.2 | 170 | NIL | 0.2 | 40 | 936 | 102
2013-04-16 | 8.02 | 38 | 0.2 | 1985 | 1390 | 918 | 694 | 224 | 160 | 7.2 | 180 | NIL | 0.3 | 75 | 921 | 108
2013-04-17 | 7.89 | 29 | 0.2 | 2084 | 1459 | 938 | 550 | 388 | 164 | 7.1 | 165 | NIL | 0.3 | 76 | 910 | 105
2013-04-18 | 7.8 | 24 | 0.2 | 2142 | 1500 | 971 | 571 | 400 | 171 | 7 | 160 | NIL | 0.2 | 45 | 924 | 108
2013-04-19 | 7.8 | 39 | 0.2 | 2150 | 1504 | 1089 | 679 | 410 | 175 | 5.8 | 160 | NIL | 0.2 | 76 | 930 | 110
2013-04-20 | 7.96 | 60 | 0.2 | 2140 | 1495 | 969 | 575 | 394 | 175 | 5.7 | 170 | NIL | 0.2 | 110 | 935 | 113
2013-04-21 | 8.05 | 23 | 0.2 | 2142 | 1500 | 990 | 580 | 410 | 178 | 5.9 | 180 | NIL | 0.2 | 50 | 960 | 115
2013-04-22 | 7.99 | 26 | 0.2 | 2850 | 1995 | 1040 | 582 | 458 | 189 | 7.2 | 185 | NIL | 0.2 | 45 | 946 | 121
2013-04-23 | 7.98 | 23 | 0.2 | 2690 | 1883 | 986 | 574 | 412 | 178 | 7.1 | 182 | NIL | 0.2 | 42 | 930 | 118
2013-04-24 | 7.97 | 19 | 0.2 | 2880 | 1960 | 1019 | 624 | 395 | 189 | 7 | 180 | NIL | 0.2 | 35 | 912 | 111
2013-04-25 | 8.02 | 18 | 0.2 | 2571 | 1800 | 953 | 562 | 391 | 164 | 7 | 185 | NIL | 0.2 | 30 | 898 | 102
2013-04-26 | 7.98 | 35 | 0.2 | 2592 | 1815 | 1019 | 603 | 416 | 174 | 7 | 170 | NIL | 0.2 | 62 | 915 | 108
2013-04-27 | 7.89 | 30 | 0.2 | 2595 | 1816 | 1027 | 611 | 416 | 178 | 7.1 | 165 | NIL | 0.2 | 60 | 930 | 110
2013-04-28 | 7.9 | 32 | 0.2 | 2600 | 1818 | 1028 | 613 | 415 | 176 | 7.3 | 160 | NIL | 0.2 | 62 | 935 | 115
2013-04-29 | 7.98 | 31 | 0.2 | 2685 | 1880 | 1040 | 624 | 416 | 178 | 7.1 | 170 | NIL | 0.2 | 63 | 943 | 120
2013-04-30 | 7.98 | 24 | 0.2 | 2427 | 1699 | 899 | 556 | 343 | 153 | 7.2 | 170 | NIL | 0.2 | 44 | 918 | 110
MIN. | 7.59 | 18 | 0.1 | 1740 | 1218 | 672 | 401 | 224 | 103 | 5.7 | 120 | 0 | 0.2 | 30 | 893 | 91
MAX. | 8.12 | 121 | 0.2 | 2880 | 1995 | 1102 | 694 | 458 | 196 | 8 | 185 | 0 | 0.3 | 240 | 984 | 121
AVG. | 7.939 | 45.8333 | 0.19667 | 2251.8 | 1560.4 | 904.4333 | 538.8333 | 365.6 | 152.0333 | 6.94 | 166.7333 |  | 0.20667 | 89.4 | 932.8 | 109.0333
No. of < Spec | 0 | -- | 1 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 6 | 28 | 0 | -- | 0 | 0 | -- | -- | 0 | 27 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- | 3.3333 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | --
% > Specs. | 20 | 93.3333 | 0 |  | 0 | 0 |  | -- | 0 | 90 | 0 |  | 0 |  | 0 | 0