## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2 | COC
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm | Based on TH
2013-08-01 | 8.01 | 14 | 0.1 | 2371 | 1660 | 805 | 509 | 296 | 174 | 7.6 | 180 | NIL | 0.3 | 29 | 927 | 107 | 7.6667
2013-08-02 | 7.68 | 9 | 0.2 | 1985 | 1390 | 827 | 521 | 306 | 184 | 7.2 | 110 | NIL | 0.2 | 20 | 934 | 112 | 7.9519
2013-08-03 | 7.86 | 16 | 0.2 | 2470 | 1729 | 818 | 513 | 305 | 181 | 7.8 | 120 | NIL | 0.2 | 25 | 917 | 109 | 7.8654
2013-08-04 | 8.08 | 16 | 0.2 | 2500 | 1740 | 805 | 509 | 296 | 188 | 7.7 | 170 | NIL | 0.2 | 30 | 920 | 107 | 7.6667
2013-08-05 | 8.1 | 15 | 0.2 | 2572 | 1801 | 860 | 517 | 343 | 191 | 7.8 | 186 | NIL | 0.2 | 28 | 901 | 110 | 8.1132
2013-08-06 | 8.07 | 16 | 0.1 | 2380 | 1680 | 852 | 594 | 258 | 216 | 7.9 | 180 | NIL | 0.2 | 29 | 887 | 107 | 8.4356
2013-08-07 | 7.87 | 18 | 0.2 | 2600 | 1850 | 932 | 636 | 296 | 222 | 7.3 | 160 | NIL | 0.2 | 25 | 899 | 112 | 9.2277
2013-08-08 | 8.03 | 16 | 0.2 | 2570 | 1830 | 852 | 582 | 270 | 191 | 7.9 | 150 | NIL | 0.2 | 27 | 882 | 108 | 8.3529
2013-08-09 | 7.82 | 16 | 0.2 | 2485 | 1740 | 811 | 561 | 250 | 174 | 7.5 | 155 | NIL | 0.2 | 26 | 874 | 105 | 8.11
2013-08-10 | 7.86 | 16 | 0.1 | 2311 | 1618 | 728 | 520 | 208 | 170 | 8 | 158 | NIL | 0.2 | 28 | 887 | 100 | 7.2079
2013-08-11 | 7.87 | 14 | 0.1 | 2192 | 1535 | 805 | 509 | 296 | 167 | 7.7 | 155 | NIL | 0.2 | 24 | 890 | 174 | 7.8155
2013-08-12 | 8.02 | 17 | 0.2 | 2208 | 1546 | 665 | 457 | 208 | 142 | 7 | 168 | NIL | 0.2 | 29 | 873 | 105 | 6.65
2013-08-13 | 8.04 | 17 | 0.3 | 2251 | 1576 | 728 | 499 | 229 | 156 | 8 | 170 | NIL | 0.2 | 33 | 921 | 111 | 7.2079
2013-08-14 | 8.11 | 16 | 0.2 | 2185 | 1530 | 479 | 520 | -41 | 149 | 7.5 | 178 | NIL | 0.2 | 34 | 929 | 105 | 4.6961
2013-08-15 | 8.06 | 18 | 0.2 | 2215 | 1551 | 757 | 528 | 229 | 153 | 7.6 | 172 | NIL | 0.2 | 36 | 927 | 106 | 7.2095
2013-08-16 | 7.7 | 18 | 0.2 | 2307 | 1615 | 790 | 520 | 270 | 156 | 7.5 | 165 | NIL | 0.2 | 35 | 910 | 103 | 7.7451
2013-08-17 | 8.04 | 18 | 0.2 | 2210 | 1547 | 770 | 499 | 271 | 142 | 7.2 | 170 | NIL | 0.2 | 34 | 929 | 109 | 7.6238
2013-08-18 | 7.96 | 21 | 0.2 | 2131 | 1492 | 782 | 491 | 291 | 146 | 7.1 | 160 | NIL | 0.2 | 42 | 923 | 102 | 7.5922
2013-08-19 | 7.98 | 18 | 0.2 | 1914 | 1340 | 715 | 470 | 245 | 139 | 7.9 | 162 | NIL | 0.2 | 33 | 932 | 107 | 6.7453
2013-08-20 | 7.87 | 18 | 0.2 | 1985 | 1390 | 686 | 457 | 229 | 132 | 7.8 | 150 | NIL | 0.2 | 37 | 912 | 104 | 6.7255
2013-08-21 | 7.93 | 18 | 0.2 | 2157 | 1510 | 757 | 441 | 316 | 142 | 7.5 | 158 | NIL | 0.2 | 39 | 902 | 112 | 7.495
2013-08-22 | 8.02 | 19 | 0.2 | 2137 | 1496 | 782 | 491 | 291 | 153 | 7.9 | 162 | NIL | 0.2 | 37 | 927 | 107 | 7.4476
2013-08-23 | 7.49 | 18 | 0.2 | 2214 | 1550 | 836 | 540 | 296 | 142 | 7 | 100 | NIL | 0.2 | 34 | 937 | 110 | 8.36
2013-08-24 | 7.84 | 18 | 0.2 | 2068 | 1448 | 749 | 499 | 250 | 139 | 7.7 | 140 | NIL | 0.2 | 36 | 910 | 108 | 7.5657
2013-08-25 | 7.78 | 20 | 0.2 | 2090 | 1463 | 757 | 516 | 241 | 142 | 7.6 | 120 | NIL | 0.2 | 40 | 925 | 111 | 7.0748
2013-08-26 | 7.99 | 18 | 0.1 | 2171 | 1520 | 790 | 486 | 304 | 139 | 7.9 | 150 | NIL | 0.2 | 35 | 939 | 114 | 7.9
2013-08-27 | 7.85 | 20 | 0.1 | 2128 | 1490 | 778 | 478 | 300 | 132 | 7.3 | 140 | NIL | 0.2 | 42 | 914 | 107 | 7.8586
2013-08-28 | 7.9 | 19 | 0.2 | 2127 | 1489 | 775 | 498 | 277 | 142 | 7.8 | 160 | NIL | 0.2 | 37 | 922 | 105 | 7.598
2013-08-29 | 8.1 | 18 | 0.2 | 2014 | 1410 | 715 | 437 | 278 | 125 | 7.9 | 182 | NIL | 0.2 | 32 | 890 | 98 | 7.5263
2013-08-30
2013-08-31
MIN. | 7.49 | 9 | 0.1 | 1914 | 1340 | 479 | 437 | -41 | 125 | 7 | 100 | 0 | 0.2 | 20 | 873 | 98 | 4.6961
MAX. | 8.11 | 21 | 0.3 | 2600 | 1850 | 932 | 636 | 343 | 222 | 8 | 186 | 0 | 0.3 | 42 | 939 | 174 | 9.2277
AVG. | 7.9286 | 17.069 | 0.18276 | 2239.5862 | 1570.2069 | 772.6207 | 510.2759 | 262.3448 | 159.6207 | 7.6069 | 156.2414 |  | 0.20345 | 32.2759 | 911.7241 | 109.4828 | 7.5667
No. of < Spec | 1 | -- | 6 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | -- | --
No. of > Spec | 12 | 1 | 0 | -- | 0 | 0 | -- | -- | 0 | 29 | 0 | -- | 0 | -- | 0 | 0 | 0
% < Specs. | 3.4483 | -- | 20.6897 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | -- | --
% > Specs. | 41.3793 | 3.4483 | 0 |  | 0 | 0 |  | -- | 0 | 100 | 0 |  | 0 |  | 0 | 0 | 0