## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2 | COC
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm | Based on TH
2014-02-01 | 7.98 | 19 | 0.3 | 2253 | 1510 | 745 | 454 | 291 | 99 | 7.1 | 140 | NIL | 0.2 | 39 | 891 | 107 | 5.7308
2014-02-02 | 8.03 | 22 | 0.3 | 2249 | 1507 | 737 | 445 | 292 | 99 | 7.1 | 150 | NIL | 0.2 | 45 | 895 | 105 | 5.4593
2014-02-03 | 8.14 | 22 | 0.3 | 2244 | 1504 | 824 | 502 | 322 | 103 | 7 | 160 | NIL | 0.2 | 45 | 873 | 101 | 6.2424
2014-02-04 | 8.23 | 22 | 0.3 | 2252 | 1509 | 815 | 497 | 318 | 103 | 7.1 | 170 | NIL | 0.2 | 44 | 882 | 103 | 6.2692
2014-02-05 | 8.23 | 22 | 0.3 | 2417 | 1620 | 828 | 505 | 323 | 106 | 7 | 175 | NIL | 0.2 | 46 | 903 | 106 | 6.3206
2014-02-06 | 7.98 | 20 | 0.3 | 2238 | 1500 | 844 | 575 | 269 | 108 | 7 | 140 | NIL | 0.2 | 41 | 911 | 108 | 6.3939
2014-02-07 | 8.1 | 21 | 0.3 | 2313 | 1550 | 865 | 527 | 338 | 121 | 7.2 | 160 | NIL | 0.2 | 42 | 914 | 111 | 6.5038
2014-02-08 | 8.06 | 22 | 0.3 | 2343 | 1570 | 873 | 536 | 337 | 125 | 7.1 | 150 | NIL | 0.2 | 45 | 915 | 101 | 6.3261
2014-02-09 | 8.02 | 22 | 0.3 | 2328 | 1560 | 878 | 541 | 337 | 129 | 7.2 | 155 | NIL | 0.2 | 46 | 923 | 105 | 6.5522
2014-02-10 | 8.05 | 22 | 0.3 | 2283 | 1530 | 865 | 527 | 338 | 125 | 7.3 | 158 | NIL | 0.2 | 47 | 915 | 103 | 6.553
2014-02-11 | 8.1 | 22 | 0.3 | 2268 | 1520 | 873 | 541 | 332 | 124 | 7 | 160 | NIL | 0.3 | 48 | 903 | 104 | 6.4667
2014-02-12 | 8.18 | 20 | 0.3 | 2208 | 1540 | 869 | 543 | 326 | 129 | 7.1 | 165 | NIL | 0.2 | 42 | 910 | 108 | 6.4851
2014-02-13 | 8.09 | 24 | 0.3 | 2208 | 1480 | 906 | 552 | 354 | 106 | 7.2 | 160 | NIL | 0.2 | 46 | 893 | 107 | 7.0233
2014-02-14 | 8.12 | 22 | 0.3 | 2291 | 1535 | 882 | 538 | 344 | 95 | 7 | 165 | NIL | 0.2 | 48 | 880 | 102 | 6.8906
2014-02-15 | 8.02 | 20 | 0.3 | 2328 | 1560 | 845 | 515 | 330 | 103 | 7.5 | 155 | NIL | 0.2 | 42 | 894 | 105 | 6.5504
2014-02-16 | 7.98 | 20 | 0.3 | 2305 | 1545 | 840 | 519 | 321 | 100 | 7.4 | 140 | NIL | 0.2 | 39 | 885 | 102 | 6.72
2014-02-17 | 8.08 | 22 | 0.3 | 2291 | 1535 | 845 | 538 | 307 | 110 | 7.4 | 155 | NIL | 0.2 | 42 | 880 | 107 | 6.5504
2014-02-18 | 8.03 | 21 | 0.3 | 2305 | 1545 | 855 | 528 | 327 | 107 | 7.3 | 152 | NIL | 0.2 | 40 | 887 | 103 | 6.5267
2014-02-19 | 8.08 | 22 | 0.3 | 2343 | 1570 | 865 | 538 | 327 | 115 | 7.2 | 160 | NIL | 0.2 | 38 | 894 | 105 | 6.7578
2014-02-20 | 8.02 | 22 | 0.3 | 2328 | 1560 | 836 | 556 | 280 | 109 | 7.1 | 165 | NIL | 0.2 | 37 | 886 | 102 | 6.2857
2014-02-21 | 8.05 | 20 | 0.3 | 2365 | 1585 | 840 | 560 | 280 | 107 | 7.2 | 155 | NIL | 0.2 | 36 | 880 | 104 | 6.5625
2014-02-22 | 8.05 | 20 | 0.3 | 2595 | 1738 | 985 | 680 | 305 | 110 | 7.1 | 165 | NIL | 0.2 | 35 | 894 | 104 | 7.5191
2014-02-23 | 8.11 | 19 | 0.3 | 2529 | 1695 | 981 | 676 | 305 | 107 | 7 | 158 | NIL | 0.2 | 38 | 889 | 105 | 7.6641
2014-02-24 | 8.14 | 15 | 0.3 | 2516 | 1686 | 972 | 672 | 300 | 162 | 7.1 | 155 | NIL | 0.2 | 35 | 880 | 107 | 7.4769
2014-02-25 | 7.95 | 14 | 0.2 | 2373 | 1590 | 960 | 618 | 342 | 121 | 7.4 | 158 | NIL | 0.2 | 34 | 912 | 112 | 7.5
2014-02-26 | 8.12 | 21 | 0.3 | 2341 | 1569 | 976 | 622 | 354 | 110 | 7.6 | 130 | NIL | 0.2 | 31 | 965 | 119 | 7.625
2014-02-27 | 7.93 | 23 | 0.3 | 2985 | 2000 | 1030 | 663 | 367 | 132 | 7.8 | 165 | NIL | 0.2 | 35 | 998 | 127 | 7.9845
2014-02-28
MIN. | 7.93 | 14 | 0.2 | 2208 | 1480 | 737 | 445 | 269 | 95 | 7 | 130 | 0 | 0.2 | 31 | 873 | 101 | 5.4593
MAX. | 8.23 | 24 | 0.3 | 2985 | 2000 | 1030 | 680 | 367 | 162 | 7.8 | 175 | 0 | 0.3 | 48 | 998 | 127 | 7.9845
AVG. | 8.0693 | 20.7778 | 0.2963 | 2351.8148 | 1578.2593 | 875.3333 | 554.3704 | 320.963 | 113.5185 | 7.2037 | 156.3333 |  | 0.2037 | 40.963 | 901.9259 | 106.4074 | 6.7015
No. of < Spec | 0 | -- | 0 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | -- | --
No. of > Spec | 22 | 17 | 0 | -- | 0 | 0 | -- | -- | 0 | 27 | 0 | -- | 0 | -- | 0 | 0 | 0
% < Specs. | 0 | -- | 0 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | -- | --
% > Specs. | 81.4815 | 62.963 | 0 |  | 0 | 0 |  | -- | 0 | 100 | 0 |  | 0 |  | 0 | 0 | 0