## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2 | COC
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm | Based on TH
2014-01-01 | 8.06 | 26 | 0.4 | 2800 | 1960 | 728 | 445 | 283 | 110 | 7.6 | 170 | NIL | 0.2 | 58 | 881 | 98 | 5.6
2014-01-02 | 8.1 | 22 | 0.3 | 2814 | 1970 | 749 | 457 | 292 | 114 | 7.8 | 172 | NIL | 0.2 | 55 | 896 | 99 | 5.7176
2014-01-03 | 8.08 | 22 | 0.4 | 2714 | 1900 | 728 | 444 | 284 | 106 | 7.9 | 170 | NIL | 0.2 | 50 | 841 | 97 | 5.6
2014-01-04 | 8.09 | 20 | 0.3 | 2642 | 1850 | 732 | 441 | 291 | 110 | 7.8 | 170 | NIL | 0.2 | 42 | 840 | 96 | 5.6744
2014-01-05 | 8.11 | 25 | 0.3 | 2642 | 1850 | 728 | 449 | 279 | 106 | 7.8 | 180 | NIL | 0.2 | 52 | 848 | 98 | 5.6
2014-01-06 | 7.96 | 24 | 0.3 | 2731 | 1830 | 699 | 426 | 273 | 99 | 7.5 | 165 | NIL | 0.2 | 48 | 859 | 92 | 5.3769
2014-01-07 | 8.1 | 20 | 0.3 | 2137 | 1496 | 665 | 405 | 260 | 95 | 7.3 | 180 | NIL | 0.2 | 43 | 832 | 87 | 5.32
2014-01-08 | 7.98 | 22 | 0.3 | 2447 | 1640 | 707 | 431 | 276 | 103 | 7.7 | 170 | NIL | 0.2 | 45 | 859 | 89 | 5.4806
2014-01-09 | 7.96 | 15 | 0.3 | 2321 | 1625 | 736 | 449 | 287 | 106 | 7.5 | 168 | NIL | 0.2 | 32 | 869 | 98 | 5.75
2014-01-10 | 8.05 | 18 | 0.3 | 2257 | 1580 | 761 | 466 | 295 | 110 | 7.3 | 175 | NIL | 0.2 | 36 | 884 | 104 | 5.9921
2014-01-11 | 7.94 | 26 | 0.3 | 2388 | 1672 | 811 | 495 | 316 | 114 | 7.7 | 168 | NIL | 0.3 | 53 | 899 | 106 | 6.488
2014-01-12 | 7.96 | 22 | 0.3 | 2457 | 1720 | 807 | 491 | 316 | 105 | 7.4 | 165 | NIL | 0.2 | 46 | 884 | 110 | 6.2558
2014-01-13 | 7.82 | 23 | 0.3 | 2514 | 1760 | 799 | 482 | 317 | 117 | 7.2 | 158 | NIL | 0.2 | 48 | 889 | 104 | 6.2422
2014-01-14 | 7.98 | 24 | 0.3 | 2471 | 1730 | 836 | 528 | 308 | 106 | 7.3 | 165 | NIL | 0.2 | 52 | 896 | 105 | 6.5827
2014-01-15 | 7.94 | 27 | 0.3 | 2612 | 1829 | 815 | 507 | 308 | 114 | 7.2 | 163 | NIL | 0.2 | 53 | 890 | 98 | 6.52
2014-01-16 | 7.97 | 28 | 0.2 | 2708 | 1896 | 882 | 538 | 344 | 110 | 7.2 | 165 | NIL | 0.2 | 58 | 902 | 103 | 6.8906
2014-01-17 | 8.14 | 32 | 0.3 | 2600 | 1820 | 915 | 558 | 357 | 121 | 7 | 182 | NIL | 0.2 | 75 | 918 | 109 | 7.2047
2014-01-18 | 8.05 | 46 | 0.3 | 2712 | 1899 | 948 | 578 | 370 | 117 | 7.3 | 170 | NIL | 0.2 | 89 | 926 | 112 | 7.4062
2014-01-19 | 8.1 | 63 | 0.3 | 2400 | 1680 | 944 | 574 | 370 | 121 | 7.2 | 175 | NIL | 0.2 | 101 | 930 | 110 | 7.0448
2014-01-20 | 8.02 | 53 | 0.3 | 2284 | 1601 | 665 | 405 | 260 | 95 | 7.5 | 170 | NIL | 0.2 | 98 | 904 | 105 | 5.1953
2014-01-21 | 8.05 | 48 | 0.3 | 2214 | 1550 | 699 | 426 | 273 | 99 | 7.6 | 172 | NIL | 0.2 | 96 | 911 | 102 | 5.5039
2014-01-22 | 8.05 | 40 | 0.3 | 2185 | 1530 | 688 | 420 | 268 | 103 | 7.5 | 180 | NIL | 0.2 | 82 | 906 | 99 | 5.2923
2014-01-23 | 8.11 | 36 | 0.3 | 2200 | 1540 | 792 | 453 | 339 | 99 | 7.6 | 18 | NIL | 0.2 | 73 | 891 | 96 | 6.1875
2014-01-24 | 8.14 | 27 | 0.3 | 2014 | 1410 | 659 | 402 | 257 | 95 | 7.1 | 172 | NIL | 0.2 | 56 | 878 | 92 | 5.1085
2014-01-25 | 7.95 | 26 | 0.3 | 2064 | 1445 | 651 | 391 | 260 | 103 | 7.4 | 165 | NIL | 0.2 | 53 | 873 | 92 | 5.0077
2014-01-26 | 8.12 | 28 | 0.3 | 2071 | 1450 | 642 | 424 | 218 | 92 | 7.2 | 178 | NIL | 0.2 | 58 | 879 | 92 | 5.2195
2014-01-27 | 7.93 | 26 | 0.3 | 2114 | 1480 | 655 | 480 | 175 | 99 | 7 | 160 | NIL | 0.2 | 53 | 887 | 90 | 5.0775
2014-01-28 | 8.14 | 24 | 0.2 | 2071 | 1450 | 700 | 427 | 273 | 95 | 7.1 | 180 | NIL | 0.2 | 50 | 897 | 98 | 5.3846
2014-01-29 | 8.07 | 28 | 0.3 | 2071 | 1450 | 713 | 435 | 278 | 110 | 7 | 175 | NIL | 0.3 | 55 | 911 | 104 | 5.5271
2014-01-30 | 8.1 | 22 | 0.3 | 2100 | 1470 | 742 | 453 | 289 | 106 | 7.2 | 180 | NIL | 0.3 | 46 | 923 | 107 | 5.6641
2014-01-31 | 8.05 | 20 | 0.3 | 2114 | 1480 | 721 | 440 | 281 | 103 | 7.3 | 172 | Nil | 0.2 | 42 | 904 | 110 | 5.3407
MIN. | 7.82 | 15 | 0.2 | 2014 | 1410 | 642 | 391 | 175 | 92 | 7 | 18 | 0 | 0.2 | 32 | 832 | 87 | 5.0077
MAX. | 8.14 | 63 | 0.4 | 2814 | 1970 | 948 | 578 | 370 | 121 | 7.9 | 182 | 0 | 0.3 | 101 | 930 | 112 | 7.4062
AVG. | 8.0361 | 28.4839 | 0.3 | 2382.871 | 1663.3226 | 752.1613 | 461.9355 | 290.2258 | 105.9032 | 7.3935 | 166.2258 |  | 0.20968 | 58 | 887.3226 | 100.0645 | 5.847
No. of < Spec | 0 | -- | 0 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | -- | --
No. of > Spec | 20 | 26 | 0 | -- | 0 | 0 | -- | -- | 0 | 31 | 0 | -- | 0 | -- | 0 | 0 | 0
% < Specs. | 0 | -- | 0 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | -- | --
% > Specs. | 64.5161 | 83.871 | 0 |  | 0 | 0 |  | -- | 0 | 100 | 0 |  | 0 |  | 0 | 0 | 0