## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2 | COC
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm | Based on TH
2013-06-01 | 7.91 | 54 | 0.2 | 2550 | 1782 | 663 | 412 | 251 | 139 | 7.6 | 170 | NIL | 0.2 | 103 | 928 | 108 | 5.6186
2013-06-02 | 7.87 | 48 | 0.2 | 2622 | 1836 | 659 | 334 | 325 | 146 | 7.7 | 168 | NIL | 0.2 | 101 | 933 | 93 | 5.6325
2013-06-03 | 8.01 | 36 | 0.2 | 2442 | 1710 | 704 | 317 | 387 | 157 | 7.6 | 180 | NIL | 0.2 | 98 | 938 | 112 | 5.9661
2013-06-04 | 8.09 | 42 | 0.2 | 2371 | 1660 | 659 | 305 | 354 | 150 | 7.6 | 185 | NIL | 0.2 | 100 | 921 | 108 | 5.4917
2013-06-05 | 7.92 | 30 | 0.2 | 2228 | 1560 | 638 | 329 | 309 | 135 | 7.5 | 172 | NIL | 0.2 | 86 | 908 | 110 | 5.3167
2013-06-06 | 7.98 | 31 | 0.2 | 2192 | 1535 | 618 | 321 | 297 | 128 | 7.5 | 180 | NIL | 0.2 | 88 | 918 | 107 | 5.2373
2013-06-07 | 7.9 | 27 | 0.2 | 2282 | 1598 | 634 | 342 | 292 | 132 | 7.5 | 170 | NIL | 0.2 | 76 | 925 | 111 | 5.2833
2013-06-08 | 7.94 | 26 | 0.2 | 2157 | 1510 | 618 | 330 | 288 | 125 | 7.6 | 172 | NIL | 0.2 | 55 | 908 | 104 | 5.2373
2013-06-09 | 7.8 | 22 | 0.2 | 2138 | 1497 | 615 | 377 | 238 | 125 | 7.5 | 160 | NIL | 0.2 | 53 | 909 | 102 | 5.1681
2013-06-10 | 7.85 | 22 | 0.2 | 2285 | 1600 | 618 | 346 | 272 | 121 | 7.5 | 165 | NIL | 0.2 | 51 | 902 | 100 | 5.1933
2013-06-11 | 7.88 | 23 | 0.2 | 2407 | 1650 | 659 | 367 | 292 | 128 | 7.4 | 168 | NIL | 0.2 | 48 | 918 | 104 | 5.5378
2013-06-12 | 7.8 | 25 | 0.2 | 2350 | 1645 | 700 | 383 | 317 | 139 | 7.5 | 160 | NIL | 0.2 | 52 | 931 | 107 | 5.9829
2013-06-13 | 7.95 | 20 | 0.2 | 2157 | 1510 | 618 | 396 | 222 | 132 | 7.6 | 172 | NIL | 0.2 | 43 | 915 | 108 | 5.2373
2013-06-14 | 7.98 | 25 | 0.2 | 2321 | 1625 | 626 | 350 | 276 | 128 | 7.5 | 180 | NIL | 0.2 | 46 | 903 | 105 | 5.3051
2013-06-15 | 8.07 | 25 | 0.2 | 2460 | 1722 | 679 | 370 | 309 | 132 | 7.6 | 185 | NIL | 0.2 | 48 | 928 | 109 | 5.6583
2013-06-16 | 7.89 | 25 | 0.2 | 2462 | 1724 | 659 | 305 | 354 | 128 | 7.6 | 175 | NIL | 0.2 | 51 | 915 | 107 | 5.5378
2013-06-17
2013-06-18
2013-06-19
2013-06-20
2013-06-21
2013-06-22
2013-06-23 | 7.9 | 25 | 0 | 1114 | 780 | 391 | 206 | 185 | 89 | 5 | 168 | NIL | 0.2 | 53 | 314 | 60 | 3.4
2013-06-24 | 7.8 | 42 | 0 | 1514 | 1060 | 486 | 247 | 239 | 103 | 10 | 160 | NIL | 0.2 | 67 | 456 | 73 | 4.1897
2013-06-25 | 7.8 | 39 | 0.2 | 1600 | 1120 | 474 | 268 | 206 | 110 | 8 | 162 | NIL | 0.2 | 63 | 501 | 81 | 4.0513
2013-06-26 | 7.84 | 45 | 0.2 | 1732 | 1213 | 535 | 288 | 247 | 135 | 7.5 | 165 | NIL | 0.2 | 76 | 536 | 90 | 4.6121
2013-06-27 | 7.9 | 40 | 0.2 | 1714 | 1200 | 515 | 280 | 235 | 132 | 7.4 | 172 | NIL | 0.2 | 72 | 672 | 93 | 4.4017
2013-06-28 | 7.8 | 30 | 0.2 | 1857 | 1300 | 638 | 329 | 309 | 150 | 7.2 | 160 | NIL | 0.2 | 55 | 723 | 95 | 5.5
2013-06-29 | 7.96 | 33 | 0.2 | 2042 | 1430 | 650 | 337 | 313 | 160 | 7.3 | 175 | NIL | 0.2 | 50 | 773 | 97 | 5.6034
2013-06-30 | 7.76 | 30 | 0.2 | 1975 | 1383 | 659 | 342 | 317 | 168 | 7.5 | 160 | NIL | 0.2 | 47 | 779 | 93 | 5.6325
MIN. | 7.76 | 20 | 0 | 1114 | 780 | 391 | 206 | 185 | 89 | 5 | 160 | 0 | 0.2 | 43 | 314 | 60 | 3.4
MAX. | 8.09 | 54 | 0.2 | 2622 | 1836 | 704 | 412 | 387 | 168 | 10 | 185 | 0 | 0.2 | 103 | 938 | 112 | 5.9829
AVG. | 7.9 | 31.875 | 0.18333 | 2123.8333 | 1485.4167 | 613.125 | 328.375 | 284.75 | 133 | 7.5292 | 170.1667 |  | 0.2 | 65.9167 | 810.5833 | 99.0417 | 5.1998
No. of < Spec | 0 | -- | 2 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | -- | --
No. of > Spec | 3 | 23 | 0 | -- | 0 | 0 | -- | -- | 0 | 23 | 0 | -- | 0 | -- | 0 | 0 | 0
% < Specs. | 0 | -- | 8.3333 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | -- | --
% > Specs. | 12.5 | 95.8333 | 0 |  | 0 | 0 |  | -- | 0 | 95.8333 | 0 |  | 0 |  | 0 | 0 | 0