## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2 | COC
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm | Based on TH
2013-10-01 | 7.69 | 17 | 0.3 | 2550 | 1780 | 861 | 525 | 336 | 222 | 7.8 | 120 | NIL | 0.3 | 35 | 907 | 111 | 7.9722
2013-10-02 | 7.96 | 17 | 0.2 | 2530 | 1760 | 852 | 520 | 332 | 229 | 7.5 | 150 | NIL | 0.2 | 34 | 892 | 107 | 8.0377
2013-10-03 | 7.85 | 18 | 0.2 | 2510 | 1730 | 861 | 540 | 321 | 223 | 7.8 | 145 | NIL | 0.2 | 37 | 913 | 113 | 7.8273
2013-10-04 | 7.98 | 18 | 0.2 | 2630 | 1835 | 832 | 516 | 316 | 230 | 7.9 | 160 | NIL | 0.2 | 37 | 922 | 115 | 7.2348
2013-10-05 | 7.92 | 17 | 0.2 | 2620 | 1820 | 890 | 543 | 347 | 233 | 7.5 | 155 | NIL | 0.2 | 36 | 910 | 113 | 7.8761
2013-10-06 | 7.9 | 16 | 0.2 | 2600 | 1810 | 899 | 547 | 352 | 223 | 7.3 | 150 | NIL | 0.2 | 35 | 912 | 112 | 7.8174
2013-10-07 | 7.86 | 16 | 0.2 | 2550 | 1780 | 882 | 538 | 344 | 212 | 7.7 | 145 | NIL | 0.2 | 33 | 899 | 107 | 7.6034
2013-10-08 | 8.01 | 16 | 0.2 | 2510 | 1730 | 869 | 525 | 344 | 229 | 7.2 | 165 | NIL | 0.2 | 31 | 884 | 102 | 7.5565
2013-10-09 | 7.96 | 17 | 0.3 | 2500 | 1720 | 890 | 543 | 347 | 233 | 7.7 | 160 | NIL | 0.3 | 35 | 906 | 104 | 7.4167
2013-10-10 | 7.91 | 16 | 0.2 | 2520 | 1750 | 878 | 545 | 333 | 226 | 7.1 | 155 | NIL | 0.2 | 32 | 917 | 101 | 7.1967
2013-10-11 | 7.93 | 16 | 0.2 | 2515 | 1732 | 865 | 528 | 337 | 216 | 7.5 | 158 | NIL | 0.2 | 31 | 923 | 98 | 7.0325
2013-10-12 | 8.1 | 16 | 0.2 | 2630 | 1826 | 975 | 595 | 380 | 234 | 7.8 | 170 | NIL | 0.3 | 30 | 934 | 107 | 7.8
2013-10-13 | 7.98 | 17 | 0.2 | 2410 | 1683 | 890 | 525 | 365 | 233 | 7.1 | 160 | NIL | 0.2 | 33 | 922 | 112 | 7.1774
2013-10-14 | 8.02 | 18 | 0.2 | 2520 | 1750 | 912 | 556 | 356 | 213 | 7.8 | 155 | NIL | 0.2 | 38 | 927 | 111 | 7.4146
2013-10-15 | 7.96 | 15 | 0.2 | 2530 | 1760 | 903 | 550 | 353 | 216 | 7.4 | 152 | NIL | 0.2 | 31 | 921 | 115 | 7.2823
2013-10-16 | 7.9 | 16 | 0.2 | 2520 | 1718 | 924 | 555 | 369 | 223 | 7.8 | 150 | NIL | 0.2 | 32 | 936 | 118 | 7.5738
2013-10-17 | 8.09 | 18 | 0.2 | 2530 | 1731 | 890 | 564 | 326 | 198 | 7.7 | 168 | NIL | 0.2 | 36 | 918 | 109 | 7.2358
2013-10-18 | 8.02 | 18 | 0.1 | 2540 | 1745 | 903 | 551 | 352 | 194 | 7.5 | 165 | NIL | 0.3 | 36 | 905 | 110 | 7.224
2013-10-19 | 7.92 | 16 | 0.2 | 2530 | 1731 | 945 | 576 | 369 | 205 | 8 | 150 | NIL | 0.3 | 32 | 920 | 113 | 7.56
2013-10-20 | 8.12 | 15 | 0.2 | 2550 | 1780 | 954 | 661 | 293 | 205 | 7.8 | 175 | NIL | 0.2 | 30 | 905 | 105 | 7.4531
2013-10-21 | 7.95 | 18 | 0.2 | 2500 | 1720 | 945 | 576 | 369 | 198 | 7.8 | 165 | NIL | 0.2 | 36 | 916 | 103 | 7.1591
2013-10-22 | 8.02 | 18 | 0.2 | 2540 | 1745 | 931 | 578 | 353 | 205 | 7.6 | 170 | NIL | 0.2 | 35 | 909 | 109 | 6.8456
2013-10-23 | 7.92 | 18 | 0.2 | 2535 | 1740 | 979 | 597 | 382 | 234 | 7.1 | 165 | NIL | 0.2 | 34 | 926 | 113 | 7.0942
2013-10-24 | 7.89 | 18 | 0.3 | 2530 | 1762 | 996 | 607 | 389 | 252 | 7.5 | 160 | NIL | 0.3 | 33 | 948 | 117 | 7.1143
2013-10-25 | 8.25 | 19 | 0.2 | 2490 | 1710 | 975 | 594 | 381 | 216 | 7.9 | 185 | NIL | 0.2 | 39 | 932 | 114 | 6.7241
2013-10-26 | 7.98 | 18 | 0.2 | 2638 | 1838 | 958 | 585 | 373 | 205 | 7.8 | 170 | NIL | 0.3 | 37 | 919 | 112 | 6.6528
2013-10-27 | 7.82 | 19 | 0.3 | 2680 | 1870 | 967 | 598 | 369 | 219 | 7.7 | 145 | NIL | 0.3 | 38 | 947 | 113 | 6.669
2013-10-28 | 8.02 | 18 | 0.2 | 2630 | 1835 | 975 | 595 | 380 | 187 | 7.8 | 165 | NIL | 0.2 | 37 | 796 | 116 | 6.6781
2013-10-29 | 8.19 | 16 | 0.2 | 2370 | 1654 | 954 | 577 | 377 | 173 | 7.7 | 170 | NIL | 0.2 | 33 | 907 | 112 | 6.6713
2013-10-30 | 7.9 | 16 | 0.2 | 2350 | 1630 | 967 | 581 | 386 | 169 | 7.3 | 150 | NIL | 0.2 | 32 | 890 | 109 | 6.9071
2013-10-31 | 7.96 | 15 | 0.2 | 2290 | 1600 | 960 | 578 | 382 | 165 | 7.4 | 155 | NIL | 0.2 | 30 | 879 | 105
MIN. | 7.69 | 15 | 0.1 | 2290 | 1600 | 832 | 516 | 293 | 165 | 7.1 | 120 | 0 | 0.2 | 30 | 796 | 98 | 6.6528
MAX. | 8.25 | 19 | 0.3 | 2680 | 1870 | 996 | 661 | 389 | 252 | 8 | 185 | 0 | 0.3 | 39 | 948 | 118 | 8.0377
AVG. | 7.9671 | 16.9677 | 0.20968 | 2527.3548 | 1750.8065 | 918.7742 | 563.5161 | 355.2581 | 213.5484 | 7.5968 | 158.3226 |  | 0.22581 | 34.129 | 911.0323 | 109.871 | 7.2936
No. of < Spec | 0 | -- | 1 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | -- | --
No. of > Spec | 10 | 0 | 0 | -- | 0 | 0 | -- | -- | 0 | 31 | 0 | -- | 0 | -- | 0 | 0 | 0
% < Specs. | 0 | -- | 3.2258 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | -- | --
% > Specs. | 32.2581 | 0 | 0 |  | 0 | 0 |  | -- | 0 | 100 | 0 |  | 0 |  | 0 | 0 | 0