## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2 | COC
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm | Based on TH
2013-09-01 | 7.9 | 45 | 0 | 2000 | 1410 | 751 | 459 | 292 | 134 | 6.6 | 185 | NIL | 0.1 | 88 | 777 | 80 | 7.51
2013-09-02 | 7.95 | 43 | 0 | 1820 | 1210 | 749 | 457 | 292 | 134 | 6.5 | 190 | NIL | 0.1 | 82 | 821 | 85 | 7.5657
2013-09-03 | 7.83 | 53 | 0.2 | 2070 | 1405 | 736 | 437 | 299 | 145 | 7 | 180 | NIL | 0.2 | 101 | 876 | 102 | 7.0095
2013-09-04 | 7.98 | 28 | 0.2 | 2000 | 1350 | 645 | 393 | 252 | 127 | 8 | 190 | NIL | 0.2 | 50 | 851 | 89 | 6.45
2013-09-05 | 7.97 | 42 | 0.2 | 2010 | 1360 | 616 | 378 | 238 | 117 | 8.4 | 188 | NIL | 0.2 | 80 | 819 | 85 | 6.2222
2013-09-06 | 7.8 | 37 | 0.2 | 1950 | 1310 | 540 | 362 | 178 | 109 | 8.5 | 178 | NIL | 0.2 | 61 | 793 | 81 | 5.4
2013-09-07 | 7.98 | 32 | 0.2 | 1890 | 1289 | 562 | 374 | 188 | 117 | 8 | 192 | NIL | 0.2 | 57 | 858 | 89 | 4.9298
2013-09-08 | 7.75 | 27 | 0.2 | 1920 | 1302 | 540 | 362 | 178 | 109 | 8.4 | 160 | NIL | 0.2 | 45 | 839 | 81 | 4.8214
2013-09-09 | 7.8 | 26 | 0.2 | 2060 | 1394 | 645 | 393 | 252 | 127 | 7 | 182 | NIL | 0.2 | 41 | 884 | 101 | 5.9174
2013-09-10 | 8.02 | 24 | 0.2 | 2050 | 1380 | 670 | 409 | 261 | 124 | 7.2 | 195 | NIL | 0.2 | 46 | 913 | 104 | 6.7
2013-09-11 | 7.93 | 24 | 0.2 | 2010 | 1355 | 686 | 418 | 268 | 141 | 7.5 | 180 | NIL | 0.2 | 42 | 928 | 106 | 6.9293
2013-09-12 | 7.96 | 20 | 0.2 | 2000 | 1350 | 707 | 431 | 276 | 148 | 7.8 | 185 | NIL | 0.2 | 30 | 908 | 111 | 6.7981
2013-09-13 | 7.86 | 21 | 0.2 | 2050 | 1388 | 749 | 457 | 292 | 159 | 7.9 | 175 | NIL | 0.2 | 33 | 896 | 113 | 7.066
2013-09-14 | 7.71 | 13 | 0.2 | 2300 | 1561 | 811 | 495 | 316 | 170 | 8 | 160 | NIL | 0.2 | 26 | 911 | 116 | 7.5093
2013-09-15 | 7.81 | 20 | 0.2 | 2260 | 1531 | 815 | 508 | 307 | 160 | 6.3 | 175 | NIL | 0.2 | 38 | 912 | 117 | 7.2768
2013-09-16 | 7.97 | 20 | 0.2 | 2310 | 1567 | 790 | 482 | 308 | 162 | 7.8 | 185 | NIL | 0.2 | 35 | 903 | 110 | 6.9298
2013-09-17 | 8.03 | 19 | 0.2 | 2260 | 1530 | 802 | 491 | 311 | 169 | 7.9 | 195 | NIL | 0.2 | 29 | 910 | 112 | 7.0973
2013-09-18 | 7.82 | 18 | 0.2 | 2250 | 1525 | 782 | 477 | 305 | 162 | 7.5 | 172 | NIL | 0.2 | 32 | 897 | 108 | 6.9821
2013-09-19 | 7.9 | 17 | 0.3 | 2230 | 1510 | 770 | 460 | 310 | 168 | 7.3 | 180 | NIL | 0.3 | 35 | 890 | 105 | 6.6379
2013-09-20 | 7.8 | 19 | 0.2 | 2215 | 1500 | 753 | 470 | 283 | 173 | 7.2 | 170 | NIL | 0.2 | 39 | 892 | 106 | 6.3814
2013-09-21 | 7.84 | 18 | 0.2 | 2280 | 1544 | 852 | 545 | 307 | 212 | 7 | 175 | NIL | 0.2 | 42 | 913 | 112 | 7.1
2013-09-22 | 7.93 | 18 | 0.2 | 2240 | 1520 | 844 | 549 | 295 | 219 | 7.1 | 186 | NIL | 0.2 | 38 | 918 | 110 | 7.1525
2013-09-23 | 7.95 | 19 | 0.3 | 2250 | 1523 | 757 | 478 | 279 | 184 | 7.4 | 183 | NIL | 0.2 | 36 | 917 | 112 | 6.5259
2013-09-24 | 7.95 | 18 | 0.2 | 2348 | 1590 | 765 | 466 | 299 | 191 | 7.3 | 185 | NIL | 0.2 | 33 | 920 | 109 | 6.7105
2013-09-25 | 7.65 | 18 | 0.2 | 2389 | 1618 | 755 | 477 | 278 | 212 | 7 | 160 | NIL | 0.2 | 37 | 910 | 105 | 6.3983
2013-09-26 | 7.85 | 18 | 0.2 | 2487 | 1684 | 790 | 482 | 308 | 293 | 7.4 | 175 | NIL | 0.2 | 39 | 919 | 112 | 6.5833
2013-09-27 | 7.95 | 18 | 0.3 | 2658 | 1800 | 869 | 540 | 329 | 322 | 7.5 | 185 | NIL | 0.2 | 40 | 929 | 116 | 7.6228
2013-09-28 | 8.03 | 18 | 0.2 | 2568 | 1739 | 832 | 499 | 333 | 212 | 7.4 | 192 | NIL | 0.2 | 34 | 910 | 109 | 7.5636
2013-09-29 | 7.98 | 18 | 0.2 | 2496 | 1690 | 811 | 508 | 303 | 205 | 7.3 | 186 | NIL | 0.2 | 30 | 912 | 116 | 7.4404
2013-09-30 | 7.9 | 19 | 0.3 | 2437 | 1650 | 800 | 495 | 305 | 210 | 7 | 175 | NIL | 0.3 | 32 | 905 | 112 | 7.3394
MIN. | 7.65 | 13 | 0 | 1820 | 1210 | 540 | 362 | 178 | 109 | 6.3 | 160 | 0 | 0.1 | 26 | 777 | 80 | 4.8214
MAX. | 8.03 | 53 | 0.3 | 2658 | 1800 | 869 | 549 | 333 | 322 | 8.5 | 195 | 0 | 0.3 | 101 | 929 | 117 | 7.6228
AVG. | 7.8933 | 24.3333 | 0.2 | 2193.6 | 1486.1667 | 739.8 | 458.4 | 281.4 | 170.5 | 7.44 | 180.6333 |  | 0.2 | 45.0333 | 887.7 | 103.8 | 6.7524
No. of < Spec | 0 | -- | 2 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | -- | --
No. of > Spec | 3 | 12 | 0 | -- | 0 | 0 | -- | -- | 0 | 30 | 0 | -- | 0 | -- | 0 | 0 | 0
% < Specs. | 0 | -- | 6.6667 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | -- | --
% > Specs. | 10 | 40 | 0 |  | 0 | 0 |  | -- | 0 | 100 | 0 |  | 0 |  | 0 | 0 | 0