## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Total PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2015-01-01 | 7.9 | 11 | 0.5 | 2582 | 1730 | 1001 | 611 | 362 | 170 | 4.9 | 135 | 0 | 0.2 | 23 | 981 | 125
2015-01-02 | 7.6 | 10 | 0.5 | 2480 | 1660 | 989 | 603 | 365 | 167 | 4.8 | 110 | 0 | 0.2 | 21 | 972 | 126
2015-01-03 | 7.7 | 10 | 0.5 | 2433 | 1630 | 968 | 590 | 386 | 165 | 4.7 | 115 | 0 | 0.2 | 20 | 963 | 128
2015-01-04 | 7.6 | 11 | 0.5 | 2450 | 1640 | 970 | 592 | 381 | 167 | 4.8 | 110 | 0 | 0.2 | 21 | 969 | 129
2015-01-05 | 7.7 | 11 | 0.5 | 2525 | 1692 | 976 | 595 | 390 | 158 | 4.7 | 110 | 0 | 0.2 | 23 | 971 | 130
2015-01-06 | 7.9 | 13 | 0.5 | 2537 | 1700 | 947 | 577 | 385 | 166 | 4.7 | 130 | 0 | 0.2 | 26 | 942 | 131
2015-01-07 | 7.6 | 10 | 0.5 | 2270 | 1520 | 906 | 553 | 387 | 150 | 4.5 | 110 | 0 | 0.2 | 21 | 929 | 132
2015-01-08 | 7.8 | 9 | 0.5 | 2233 | 1496 | 898 | 548 | 388 | 143 | 4.7 | 130 | 0 | 0.2 | 19 | 937 | 133
2015-01-09 | 7.7 | 11 | 0.2 | 2420 | 1620 | 927 | 565 | 389 | 160 | 4.9 | 110 | 0 | 0.2 | 23 | 946 | 134
2015-01-10 | 7.7 | 12 | 0.2 | 2552 | 1710 | 948 | 578 | 370 | 168 | 5 | 105 | 0 | 0.2 | 25 | 955 | 135
2015-01-11 | 7.7 | 12 | 0.2 | 2565 | 1730 | 950 | 580 | 386 | 170 | 4.9 | 110 | 0 | 0.2 | 26 | 962 | 136
2015-01-12 | 7.8 | 11 | 0.3 | 2580 | 1750 | 955 | 585 | 379 | 172 | 4.8 | 115 | 0 | 0.2 | 24 | 973 | 137
2015-01-13 | 7.8 | 10 | 0.2 | 2600 | 1780 | 960 | 588 | 370 | 175 | 4.7 | 120 | 0 | 0.2 | 23 | 961 | 139
2015-01-14 | 7.8 | 11 | 0.6 | 2620 | 1810 | 985 | 595 | 370 | 178 | 4.8 | 115 | 0 | 0.2 | 25 | 948 | 140
2015-01-15 | 7.55 | 11 | 0.5 | 2810 | 1880 | 1005 | 593 | 378 | 190 | 5 | 100 | 0 | 0.3 | 23 | 926 | 141
2015-01-16 | 7.76 | 10 | 0.4 | 2582 | 1730 | 989 | 603 | 383 | 180 | 4.9 | 115 | 0 | 0.2 | 21 | 937 | 142
2015-01-17 | 7.7 | 11 | 0.3 | 2664 | 1785 | 1009 | 615 | 378 | 190 | 5 | 110 | 0 | 0.2 | 23 | 954 | 143
2015-01-18 | 7.8 | 10 | 0.2 | 2580 | 1750 | 1000 | 610 | 385 | 187 | 4.9 | 130 | 0 | 0.2 | 21 | 969 | 144
2015-01-19 | 7.7 | 10 | 0.6 | 2522 | 1690 | 985 | 610 | 376 | 185 | 4.8 | 120 | 0 | 0.2 | 20 | 960 | 145
2015-01-20 | 7.4 | 11 | 0.5 | 2420 | 1620 | 960 | 585 | 378 | 172 | 4.8 | 100 | 0 | 0.2 | 23 | 949 | 146
2015-01-21 | 7.8 | 12 | 0.5 | 2730 | 1826 | 980 | 598 | 379 | 180 | 4.9 | 120 | 0 | 0.2 | 25 | 973 | 147
2015-01-22 | 7.6 | 11 | 0.4 | 2664 | 1785 | 1000 | 610 | 381 | 182 | 4.7 | 100 | 0 | 0.2 | 23 | 967 | 146
2015-01-23 | 7.7 | 10 | 0.2 | 2635 | 1765 | 984 | 600 | 384 | 174 | 4.8 | 120 | 0 | 0.2 | 21 | 958 | 147
2015-01-24 | 7.7 | 10 | 0.3 | 2560 | 1715 | 960 | 586 | 379 | 172 | 4.8 | 105 | 0 | 0.2 | 22 | 951 | 148
2015-01-25 | 7.7 | 11 | 0.3 | 2580 | 1730 | 965 | 588 | 376 | 173 | 4.9 | 110 | 0 | 0.2 | 23 | 959 | 149
2015-01-26 | 7.8 | 11 | 0.2 | 2600 | 1750 | 970 | 590 | 383 | 175 | 4.9 | 115 | 0 | 0.2 | 23 | 965 | 150
2015-01-27 | 7.7 | 10 | 0.1 | 2638 | 1768 | 960 | 586 | 382 | 186 | 4.8 | 120 | 0 | 0.2 | 21 | 956 | 148
2015-01-28 | 7.8 | 9 | 0 | 2532 | 1693 | 952 | 580 | 388 | 180 | 4.9 | 125 | 0 | 0.2 | 19 | 947 | 146
2015-01-29 | 7.8 | 10 | 0.1 | 2552 | 1710 | 940 | 573 | 389 | 174 | 4.8 | 130 | 0 | 0.2 | 21 | 941 | 145
2015-01-30 | 7.8 | 10 | 0.1 | 2375 | 1593 | 932 | 568 | 394 | 170 | 4.9 | 125 | 0 | 0.2 | 21 | 949 | 144
2015-01-31 | 7.7 | 9 | 0.5 | 2350 | 1552 | 920 | 561 | 402 | 168 | 4.8 | 115 | 0 | 0.2 | 23 | 938 | 143
MIN. | 7.4 | 9 | 0 | 2233 | 1496 | 920 | 548 | 362 | 142 | 4.8 | 100 | 0 | 0.2 | 19 | 938 | 125
MAX. | 7.9 | 16 | 0.6 | 2810 | 1880 | 1009 | 615 | 402 | 190 | 4.6 | 135 | 0 | 0.3 | 26 | 981 | 150
AVG. | 7.7197 | 10 | 0.35161 | 2536.8065 | 1703.5484 | 964.2258 | 587.6129 | 381.3871 | 171.5312 | 4.8226 | 115.6452 | 0 | 0.20323 | 22.3548 | 955.0968 | 139.6452
No. of < Spec | 1 | -- | 4 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 0 | 2 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 3.2258 | -- | 12.9032 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | --
% > Specs. | 0 | 0 | 6.4516 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0