## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 10.0 - 12.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2014-08-01 | 7.8 | 28 | 0 | 1120 | 747 | 298 | 182 | 116 | 89 | 10.5 | 170 | NIL | 0.2 | 55 | 254 | 52
2014-08-02 | 7.73 | 26 | 0 | 1160 | 772 | 291 | 177 | 114 | 79 | 10.2 | 150 | NIL | 0.2 | 52 | 272 | 58
2014-08-03 | 7.75 | 22 | 0 | 1240 | 830 | 298 | 182 | 116 | 89 | 10.5 | 145 | NIL | 0.2 | 50 | 279 | 64
2014-08-04 | 7.8 | 24 | 0 | 1244 | 831 | 290 | 181 | 109 | 81 | 10.1 | 150 | NIL | 0.2 | 51 | 274 | 57
2014-08-05 | 7.83 | 22 | 0 | 1300 | 950 | 462 | 306 | 156 | 79 | 6.7 | 155 | NIL | 0.2 | 53 | 361 | 62
2014-08-06 | 7.91 | 20 | 0 | 1420 | 1090 | 459 | 302 | 157 | 85 | 6.7 | 150 | NIL | 0.2 | 45 | 399 | 67
2014-08-07 | 7.7 | 18 | 0 | 1650 | 1102 | 564 | 228 | 336 | 124 | 5.8 | 145 | NIL | 0.2 | 40 | 421 | 73
2014-08-08 | 7.78 | 18 | 0.1 | 1720 | 1150 | 569 | 344 | 225 | 141 | 8 | 142 | NIL | 0.2 | 38 | 487 | 76
2014-08-09 | 7.83 | 17 | 0 | 1810 | 1210 | 582 | 355 | 227 | 137 | 7.9 | 150 | NIL | 0.2 | 36 | 513 | 69
2014-08-10 | 7.7 | 18 | 0.1 | 1690 | 1130 | 582 | 302 | 280 | 137 | 5.8 | 155 | NIL | 0.2 | 38 | 510 | 67
2014-08-11 | 7.68 | 18 | 0.2 | 1830 | 1221 | 564 | 328 | 236 | 137 | 5.8 | 160 | NIL | 0.2 | 40 | 513 | 69
2014-08-12 | 7.65 | 18 | 0.1 | 1880 | 1255 | 462 | 360 | 102 | 141 | 8 | 155 | NIL | 0.2 | 41 | 510 | 61
2014-08-13 | 7.85 | 18 | 0.1 | 2090 | 1400 | 593 | 364 | 229 | 143 | 8 | 160 | NIL | 0.2 | 42 | 523 | 64
2014-08-14 | 7.7 | 17 | 0.1 | 1970 | 1320 | 590 | 360 | 230 | 137 | 7.9 | 165 | NIL | 0.2 | 37 | 532 | 65
2014-08-15 | 7.65 | 18 | 0.1 | 1970 | 1320 | 593 | 364 | 229 | 138 | 8 | 160 | NIL | 0.2 | 39 | 593 | 64
2014-08-16 | 7.6 | 18 | 0.1 | 1910 | 1280 | 586 | 357 | 229 | 138 | 7.8 | 155 | NIL | 0.2 | 38 | 518 | 63
2014-08-17 | 7.72 | 18 | 0.1 | 1850 | 1240 | 593 | 364 | 229 | 137 | 8 | 155 | NIL | 0.2 | 40 | 523 | 65
2014-08-18 | 7.6 | 18 | 0.1 | 1970 | 1320 | 590 | 364 | 226 | 137 | 8.3 | 158 | NIL | 0.2 | 41 | 510 | 63
2014-08-19 | 7.58 | 17 | 0.1 | 2020 | 1350 | 540 | 306 | 234 | 137 | 7.9 | 160 | NIL | 0.2 | 36 | 532 | 60
2014-08-20 | 7.82 | 18 | 0.1 | 1910 | 1276 | 764 | 466 | 298 | 144 | 7.8 | 165 | NIL | 0.2 | 38 | 536 | 64
2014-08-21 | 7.75 | 18 | 0.2 | 2030 | 1360 | 728 | 444 | 284 | 144 | 7 | 160 | NIL | 0.2 | 39 | 693 | 89
2014-08-22 | 7.68 | 18 | 0.2 | 2170 | 1450 | 793 | 491 | 302 | 155 | 7.1 | 165 | NIL | 0.2 | 37 | 698 | 78
2014-08-23 |  | 16 | 0.2 | 2270 | 1520 | 782 | 477 | 305 | 151 | 7.8 | 170 | NIL | 0.2 | 33 | 811 | 75
2014-08-24 |  | 18 | 0.2 | 2020 | 1350 | 764 | 466 | 298 | 144 | 7.8 | 165 | NIL | 0.2 | 36 | 811 | 64
2014-08-25 |  | 18 | 0.2 | 2322 | 1556 | 837 | 510 | 327 | 155 | 7.8 | 165 | NIL | 0.2 | 34 | 807 | 75
2014-08-26 | 7.62 | 17 | 0.2 | 2150 | 1440 | 910 | 555 | 355 | 158 | 7.3 | 160 | NIL | 0.2 | 39 | 824 | 79
2014-08-27 | 7.56 | 18 | 0.1 | 2328 | 1560 | 892 | 544 | 348 | 168 | 7.6 | 155 | NIL | 0.2 | 40 | 837 | 76
2014-08-28 | 7.5 | 18 | 0.1 | 2360 | 1580 | 899 | 548 | 351 | 165 | 7.7 | 158 | NIL | 0.2 | 42 | 796 | 77
2014-08-29 | 7.43 | 17 | 0 | 2360 | 1580 | 910 | 555 | 355 | 165 | 7.3 | 160 | NIL | 0.2 | 35 | 829 | 76
2014-08-30 | 7.7 | 18 | 0 | 2320 | 1548 | 848 | 535 | 313 | 148 | 7.7 | 165 | NIL | 0.2 | 38 | 826 | 79
2014-08-31 | 7.8 | 18 | 0 | 2260 | 1510 | 855 | 539 | 316 | 158 | 7.5 | 165 | NIL | 0.2 | 37 | 835 | 75
MIN. | 7.43 | 17 | 0 | 1120 | 747 | 290 | 177 | 102 | 142 | 5.8 | 142 | 0 | 0.2 | 33 | 254 | 52
MAX. | 7.91 | 28 | 0.2 | 2360 | 1580 | 910 | 555 | 355 | 168 | 10.5 | 170 | 0 | 0.2 | 55 | 837 | 89
AVG. | 7.7043 | 19 | 0.087097 | 1882.0645 | 1266.0645 | 628.6452 | 382.4516 | 246.1935 | 133.8438 | 7.8161 | 157.8387 | 0 | 0.2 | 40.6452 | 575.0645 | 68.5806
No. of < Spec | 1 | -- | 24 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 5 | 0 | -- | 0 | 0 | -- | -- | 0 | 28 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 3.5714 | -- | 77.4194 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | --
% > Specs. | 0 | 16.129 | 0 |  | 0 | 0 |  | -- | 0 | 90.3226 | 0 |  | 0 |  | 0 | 0