## Sheet1
CIRCULATING WATER ANALYSIS FOR MAIN PLANT COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.09.14 | 7.94 | 18 | 0.1 | 2171 | 1520 | 855 | 539 | 316 | 158 | 7.4 | 160 | NIL | 0.2 | 37 | 836 | 75
02.09.14 | 7.92 | 18 | 0.1 | 2300 | 1610 | 837 | 510 | 327 | 144 | 7.5 | 158 | NIL | 0.2 | 36 | 806 | 94
03.09.14 | 8 | 17 | 0.1 | 2214 | 1550 | 844 | 515 | 329 | 137 | 7.8 | 165 | NIL | 0.2 | 35 | 802 | 95
04.09.14 | 7.96 | 18 | 0.1 | 2257 | 1580 | 855 | 522 | 333 | 155 | 7.5 | 160 | NIL | 0.2 | 37 | 841 | 99
05.09.14 | 7.85 | 16 | 0.1 | 2040 | 1638 | 866 | 528 | 338 | 127 | 7.8 | 155 | NIL | 0.2 | 34 | 826 | 104
06.09.14 | 7.9 | 18 | 0.1 | 2340 | 1570 | 800 | 488 | 312 | 137 | 7.9 | 162 | NIL | 0.2 | 36 | 886 | 102
07.09.14 | 7.89 | 18 | 0.1 | 2242 | 1600 | 759 | 470 | 289 | 148 | 7.9 | 160 | NIL | 0.2 | 37 | 842 | 109
08.09.14 | 7.9 | 18 | 0.2 | 2285 | 1660 | 874 | 533 | 341 | 148 | 7.9 | 125 | NIL | 0.2 | 38 | 867 | 110
09.09.14 | 7.81 | 18 | 0.1 | 2371 | 1730 | 903 | 550 | 353 | 158 | 7.8 | 162 | NIL | 0.2 | 39 | 879 | 113
10.09.14 | 7.89 | 19 | 0.1 | 2471 | 1750 | 884 | 539 | 345 | 144 | 7.5 | 150 | NIL | 0.2 | 35 | 871 | 104
11.09.14 | 7.81 | 18 | 0.1 | 2500 | 1720 | 892 | 544 | 348 | 145 | 7.8 | 155 | NIL | 0.2 | 33 | 854 | 101
12.09.14 | 7.98 | 17 | 0.1 | 2457 | 1750 | 877 | 535 | 342 | 170 | 7.8 | 150 | NIL | 0.2 | 38 | 884 | 103
13.09.14 | 7.94 | 18 | 0.1 | 2500 | 1710 | 895 | 546 | 349 | 131 | 7.9 | 165 | NIL | 0.2 | 36 | 829 | 97
14.09.14 | 7.98 | 18 | 0.1 | 2442 | 1703 | 899 | 539 | 360 | 145 | 7.4 | 162 | NIL | 0.2 | 35 | 838 | 101
15.09.14 | 7.8 | 18 | 0.1 | 2432 | 1740 | 902 | 550 | 352 | 150 | 7.9 | 170 | NIL | 0.2 | 39 | 841 | 103
16.09.14 | 7.78 | 19 | 0.1 | 2485 | 1678 | 855 | 522 | 333 | 145 | 7.8 | 150 | NIL | 0.1 | 36 | 823 | 108
17.09.14 | 7.82 | 18 | 0.1 | 2397 | 1730 | 866 | 528 | 338 | 145 | 7.7 | 145 | NIL | 0.2 | 37 | 842 | 111
18.09.14 | 7.85 | 19 | 0.1 | 2471 | 1760 | 837 | 510 | 327 | 129 | 8 | 155 | NIL | 0.2 | 35 | 847 | 105
19.09.14 | 7.95 | 18 | 0.1 | 2514 | 1750 | 848 | 517 | 331 | 126 | 7.9 | 160 | NIL | 0.2 | 39 | 813 | 109
20.09.14 | 7.82 | 19 | 0.1 | 2500 | 1806 | 946 | 577 | 369 | 152 | 7.9 | 165 | NIL | 0.2 | 36 | 821 | 114
21.09.14 | 7.95 | 18 | 0.1 | 2580 | 1770 | 939 | 597 | 342 | 149 | 7.7 | 160 | NIL | 0.2 | 35 | 826 | 111
22.09.14 | 7.8 | 18 | 0.1 | 2528 | 1763 | 903 | 557 | 346 | 135 | 7.5 | 165 | NIL | 0.2 | 37 | 894 | 113
23.09.14 | 7.88 | 19 | 0.1 | 2518 | 1740 | 866 | 528 | 338 | 135 | 7.8 | 155 | NIL | 0.2 | 39 | 852 | 110
24.09.14 | 7.85 | 18 | 0.1 | 2485 | 1695 | 873 | 532 | 341 | 135 | 7.6 | 160 | NIL | 0.2 | 41 | 867 | 107
25.09.14 | 7.7 | 19 | 0.1 | 2421 | 1624 | 837 | 510 | 327 | 129 | 7.9 | 158 | NIL | 0.2 | 38 | 819 | 110
26.09.14 | 7.98 | 18 | 0.1 | 2320 | 1685 | 855 | 521 | 334 | 135 | 7.6 | 140 | NIL | 0.2 | 36 | 823 | 102
27.09.14 | 7.95 | 18 | 0.1 | 2407 | 1678 | 848 | 517 | 331 | 145 | 7.6 | 165 | NIL | 0.2 | 33 | 829 | 109
28.09.14 | 7.92 | 18 | 0.1 | 2397 | 1640 | 837 | 520 | 317 | 135 | 7.9 | 160 | NIL | 0.2 | 32 | 830 | 102
29.09.14 | 7.96 | 18 | 0.1 | 2342 | 1680 | 882 | 538 | 344 | 138 | 7.9 | 162 | NIL | 0.2 | 38 | 873 | 112
30.09.14 | 7.76 | 18 | 0.1 | 2400 | 1696 | 819 | 499 | 320 | 152 | 7.9 | 150 | NIL | 0.2 | 35 | 811 | 110
MIN. | 7.7 | 16 | 0.1 | 2422 | 1520 | 759 | 470 | 289 | 126 | 7.4 | 150 | 0 | 0.1 | 32 | 802 | 75
MAX. | 8 | 19 | 0.2 | 2580 | 1806 | 946 | 597 | 369 | 170 | 8 | 170 | 0 | 0.2 | 41 | 894 | 114
AVG. | 7.8847 | 18.0667 | 0.10333 | 2392.9 | 1684.2 | 865.1 | 529.3667 | 335.7333 | 142.7333 | 7.75 | 156.9667 | NIL | 0.19667 | 36.4 | 842.4 | 104.7667
No. of < Spec | 0 | -- | 29 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 0 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- | 96.6667 | -- | -- | -- | -- | -- | -- | 0 | - | - | - | - | - | --
% > Specs. | 0 | 0 | 0 | - | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | - | 0 | 0