## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
01.04.16 | 7.5 | 17 | 0.1 | 1395 | 530 | 289 | 241 | 155 | 6.6 | 10.6 | 104 | 866 | 118
02.04.16 | 7.62 | 16 | 0.1 | 1380 | 549 | 293 | 256 | 152 | 6.8 | 10.8 | 110 | 861 | 117
03.04.16 | 7.58 | 18 | 0.1 | 1382 | 545 | 292 | 253 | 154 | 6.8 | 11.8 | 112 | 870 | 115
04.04.16 | 7.56 | 18 | 0.1 | 1370 | 545 | 286 | 259 | 148 | 6.8 | 11.8 | 108 | 863 | 117
05.04.16 | 7.8 | 17 | 0.1 | 1345 | 538 | 282 | 256 | 148 | 6.8 | 11.8 | 102 | 857 | 118
06.04.16 | 7.84 | 16 | 0.1 | 1335 | 534 | 278 | 256 | 141 | 6.8 | 10.8 | 104 | 863 | 117
07.04.16 | 7.7 | 16 | 0.1 | 1580 | 508 | 271 | 237 | 134 | 6.8 | 10.8 | 107 | 867 | 119
08.04.16 | 8 | 15 | 0.1 | 1460 | 500 | 267 | 233 | 127 | 7 | 10.8 | 105 | 868 | 118
09.04.16 | 7.8 | 15 | 0.1 | 1380 | 519 | 286 | 233 | 128 | 6.8 | 10.8 | 102 | 853 | 118
10.04.16 | 7.68 | 18 | 0.1 | 1390 | 534 | 278 | 256 | 127 | 6.38 | 10.8 | 106 | 870 | 119
11.04.16 | 7.7 | 18 | 0.1 | 1383 | 556 | 308 | 248 | 148 | 6.3 | 10.2 | 120 | 861 | 118
12.04.16 | 7.6 | 18 | 0.1 | 1370 | 549 | 301 | 248 | 141 | 6.2 | 10.2 | 110 | 868 | 116
13.04.16 | 7.7 | 19 | 0.1 | 1480 | 541 | 316 | 225 | 197 | 6.2 | 10.2 | 108 | 865 | 118
14.04.16 | 7.6 | 18 | 0.1 | 1470 | 632 | 372 | 260 | 198 | 6.2 | 10.21 | 122 | 857 | 117
15.04.16 | 7.8 | 19 | 0.01 | 1440 | 620 | 350 | 270 | 190 | 6.2 | 10.2 | 128 | 860 | 119
16.04.16 | 7.67 | 19 | 0.1 | 1447 | 617 | 345 | 271 | 183 | 6.3 | 10.3 | 108 | 853 | 117
17.04.16 | 7.58 | 18 | 0.1 | 1550 | 647 | 357 | 290 | 197 | 6.3 | 10.3 | 110 | 858 | 118
18.04.16 | 7.6 | 18 | 0.1 | 1518 | 658 | 346 | 312 | 204 | 6.5 | 10.5 | 104 | 868 | 119
19.04.16 | 7.89 | 22 | 0.1 | 1556 | 696 | 357 | 339 | 211 | 6.3 | 10.3 | 108 | 857 | 117
20.04.16 | 7.76 | 20 | 0.1 | 1545 | 682 | 350 | 332 | 218 | 6.3 | 10.3 | 110 | 865 | 119
21.04.16 | 7.72 | 21 | 0.1 | 1584 | 692 | 357 | 335 | 218 | 6.3 | 10.3 | 112 | 870 | 118
22.04.16 | 7.74 | 20 | 0.1 | 1576 | 699 | 361 | 338 | 225 | 6.3 | 10.3 | 114 | 873 | 119
23.04.16 | 7.7 | 19 | 0.1 | 1640 | 697 | 365 | 332 | 232 | 6.3 | 10.3 | 104 | 875 | 118
24.04.16 | 7.86 | 18 | 0.1 | 1680 | 760 | 403 | 357 | 226 | 6.3 | 10.3 | 110 | 872 | 118
25.04.16 | 7.81 | 19 | 0.1 | 1498 | 684 | 327 | 357 | 197 | 6.2 | 10.2 | 115 | 868 | 119
26.04.16 | 7.7 | 19 | 0.1 | 1662 | 701 | 385 | 316 | 232 | 6.4 | 10.4 | 102 | 865 | 118
27.04.16 | 7.65 | 19 | 0.1 | 1658 | 785 | 403 | 382 | 239 | 6.5 | 10.5 | 110 | 877 | 119
28.04.16 | 7.62 | 19 | 0.1 | 1680 | 739 | 374 | 365 | 211 | 6.3 | 10.3 | 100 | 878 | 118
29.04.16 | 7.68 | 19 | 0.1 | 1685 | 743 | 376 | 367 | 210 | 6.3 | 10.3 | 101 | 870 | 119
30.04.16 | 7.7 | 18 | 0.1 | 1650 | 739 | 365 | 374 | 218 | 6.3 | 10.3 | 104 | 872 | 118
MIN. | 7.5 | 15 | 0.01 | 1335 | 500 | 267 | 225 | 127 | 6.2 | 10.2 | 100 | 853 | 115
MAX. | 8 | 22 | 0.1 | 1685 | 785 | 403 | 382 | 239 | 7 | 11.8 | 128 | 878 | 119
No. of < Spec | 0 | -- | 30 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 2 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 0 | -- | 100 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 6.6667 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0