## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
01.05.16 | 7.48 | 19 | 0.1 | 1710 | 739 | 374 | 365 | 155 | 6.3 | 10.4 | 112 | 880 | 118
02.05.16 | 7.52 | 18 | 0.1 | 1760 | 773 | 391 | 382 | 211 | 6.3 | 10.3 | 115 | 886 | 115
03.05.16 | 7.56 | 20 | 0.1 | 1600 | 739 | 365 | 374 | 246 | 6.3 | 10.5 | 120 | 890 | 117
04.05.16 | 7.6 | 18 | 0.1 | 1700 | 727 | 361 | 366 | 239 | 6.3 | 10.4 | 118 | 898 | 116
05.05.16 | 7.7 | 20 | 0.3 | 1730 | 739 | 365 | 374 | 239 | 6.3 | 10.3 | 115 | 890 | 117
06.05.16 | 7.35 | 26 | 0.1 | 1840 | 701 | 344 | 357 | 232 | 6.3 | 10.4 | 112 | 896 | 119
07.05.16 | 7.6 | 28 | 0.1 | 1700 | 664 | 353 | 311 | 211 | 6.3 | 10.5 | 120 | 910 | 118
08.05.16 | 7.5 | 29 | 0.1 | 1720 | 659 | 357 | 302 | 218 | 6.2 | 10.3 | 118 | 905 | 119
09.05.16 | 7.6 | 22 | 0.1 | 1450 | 617 | 319 | 298 | 190 | 6.3 | 10.4 | 120 | 913 | 115
10.05.16 | 7.77 | 18 | 0.1 | 1484 | 613 | 310 | 303 | 183 | 6.3 | 10.4 | 120 | 920 | 115
11.05.16 | 7.5 | 16 | 0.3 | 1460 | 601 | 307 | 294 | 190 | 6.5 | 10.5 | 116 | 912 | 112
12.05.16 | 7.55 | 23 | 0.1 | 1400 | 592 | 302 | 290 | 183 | 6.4 | 10.4 | 115 | 902 | 114
13.05.16 | 7.59 | 20 | 0.1 | 1459 | 563 | 290 | 273 | 176 | 6.4 | 10.5 | 112 | 900 | 115
14.05.16 | 7.5 | 18 | 0.1 | 1500 | 525 | 302 | 223 | 169 | 6.5 | 10.5 | 110 | 890 | 117
15.05.16 | 7.8 | 18 | 0.1 | 1480 | 529 | 307 | 222 | 169 | 6.4 | 10.6 | 112 | 870 | 114
16.05.16 | 7.68 | 18 | 0.1 | 1776 | 590 | 328 | 268 | 190 | 6.5 | 10.5 | 115 | 880 | 115
17.05.16 | 7.56 | 19 | 0.1 | 1550 | 554 | 332 | 222 | 183 | 6.2 | 10.5 | 115 | 876 | 118
18.05.16 | 7.7 | 19 | 0.1 | 1495 | 508 | 269 | 239 | 155 | 6.3 | 10.3 | 115 | 871 | 118
19.05.16 | 7.64 | 18 | 0.1 | 1510 | 529 | 286 | 243 | 162 | 6.2 | 10.4 | 116 | 879 | 117
20.05.16 | 7.68 | 17 | 0.1 | 1490 | 525 | 273 | 252 | 155 | 6.3 | 10.3 | 114 | 870 | 115
21.05.16 | 7.58 | 18 | 0.2 | 1450 | 563 | 302 | 261 | 162 | 6.2 | 10.4 | 112 | 867 | 112
22.05.16 | 7.58 | 18 | 0.2 | 1540 | 554 | 294 | 260 | 168 | 6.2 | 10.2 | 110 | 873 | 114
23.05.16 | 7.65 | 18 | 0.2 | 1570 | 647 | 307 | 340 | 183 | 6.3 | 10.4 | 112 | 866 | 115
24.05.16 | 7.23 | 18 | 0.2 | 1501 | 643 | 302 | 341 | 169 | 6.2 | 10.5 | 112 | 862 | 114
25.05.16 | 7.48 | 17 | 0.1 | 1641 | 647 | 311 | 336 | 177 | 6.3 | 10.6 | 114 | 860 | 115
26.05.16 | 7.45 | 21 | 0.1 | 1650 | 643 | 307 | 336 | 183 | 6.2 | 10.4 | 110 | 866 | 114
27.05.16 | 7.41 | 15 | 0.2 | 1610 | 764 | 395 | 364 | 183 | 6.3 | 10.5 | 115 | 868 | 115
28.05.16 | 7.56 | 17 | 0.1 | 1670 | 735 | 365 | 370 | 211 | 6.2 | 10.5 | 118 | 876 | 114
29.05.16 | 7.59 | 20 | 0.1 | 1700 | 739 | 370 | 369 | 214 | 6.1 | 10.3 | 116 | 872 | 114
30.05.16 | 7.8 | 19 | 0.1 | 1780 | 680 | 349 | 331 | 199 | 6.3 | 10.5 | 112 | 867 | 116
31.05.16 | 7.8 | 18 | 0.1 | 1830 | 680 | 349 | 331 | 199 | 6.5 | 10.6 | 116 | 973 | 115
MIN. | 7.23 | 15 | 0.1 | 1400 | 508 | 269 | 222 | 155 | 6.1 | 10.2 | 112 | 860 | 112
MAX. | 7.8 | 29 | 0.3 | 1830 | 773 | 395 | 382 | 246 | 6.5 | 10.6 | 120 | 920 | 119
AVG. | 7.5737 | 19.5 | 0.13 | 1597.5333 | 636.7333 | 327.9 | 308.8667 | 190.1667 | 6.2967 | 10.4 | 116 | 883.8333 | 115.5667
No. of < Spec | 6 | -- | 23 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 6 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 20 | -- | 76.6667 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 20 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0