## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | Max. 1000 ppm | 180 ppm
2015-06-01 | 7.6 | 17 | NIL | 1310 | 608 | 372 | 236 | 120 | 7.5 | 120 | 0.0. | 0.2 | 719 | 93
2015-06-02 | 7.59 | 16 | 0.2 | 1289 | 620 | 378 | 230 | 129 | 7.9 | 110 | 0 | 0.2 | 743 | 90
2015-06-03 | 7.5 | 15 | 0.1 | 1250 | 612 | 373 | 239 | 137 | 7.9 | 100 | 0 | 0.2 | 732 | 93
2015-06-04 | 7.8 | 15 | 0.1 | 1256 | 580 | 354 | 226 | 129 | 7.7 | 120 | 0 | 0.2 | 746 | 97
2015-06-05 | 7.7 | 17 | 0.2 | 1310 | 592 | 361 | 231 | 146 | 7.7 | 120 | 0 | 0.2 | 783 | 99
2015-06-06 | 7.62 | 18 | 0.1 | 1350 | 580 | 354 | 226 | 154 | 7.8 | 115 | 0 | 0.2 | 799 | 102
2015-06-07 | 7.72 | 18 | 0.1 | 1380 | 592 | 361 | 231 | 146 | 7.7 | 120 | 0 | 0.2 | 783 | 99
2015-06-08 | 7.65 | 18 | 0.1 | 1390 | 584 | 364 | 216 | 155 | 7.7 | 105 | 0 | 0.2 | 732 | 102
2015-06-09 | 7.67 | 17 | 0.1 | 1501 | 592 | 360 | 232 | 163 | 7.7 | 100 | 0 | 0.2 | 745 | 100
2015-06-10 | 7.52 | 18 | 0.1 | 1650 | 608 | 371 | 237 | 189 | 7.6 | 130 | 0 | 0.2 | 786 | 98
2015-06-11 | 7.43 | 19 | 0.2 | 1800 | 840 | 512 | 328 | 172 | 7.9 | 120 | 0 | 0.2 | 811 | 105
2015-06-12 | 7.8 | 17 | 0.1 | 1760 | 844 | 512 | 332 | 189 | 7.5 | 115 | 0 | 0.2 | 820 | 100
2015-06-13 | 7.5 | 18 | 0.1 | 1840 | 852 | 520 | 332 | 180 | 7.4 | 120 | 0 | 0.2 | 828 | 102
2015-06-14 | 7.55 | 18 | 0.1 | 1790 | 860 | 528 | 332 | 172 | 7.2 | 125 | 0 | 0.2 | 834 | 105
2015-06-15 | 7.6 | 18 | 0.1 | 1820 | 872 | 540 | 332 | 180 | 7.4 | 120 | 0 | 0.2 | 845 | 108
2015-06-16 | 7.67 | 18 | NIL | 1840 | 796 | 524 | 272 | 189 | 7.5 | 115 | 0 | 0.2 | 834 | 105
2015-06-17 | 7.55 | 18 | 0.1 | 1790 | 792 | 532 | 260 | 180 | 7.9 | 110 | 0 | 0.2 | 839 | 108
2015-06-18 | 7.7 | 18 | 0.5 | 1570 | 764 | 473 | 291 | 386 | 7.4 | 105 | 0 | 0.2 | 845 | 105
2015-06-19 | 7.78 | 17 | 0.5 | 1570 | 776 | 460 | 316 | 301 | 7.2 | 120 | 0 | 0.2 | 880 | 106
2015-06-20 | 7.69 | 18 | 0.5 | 1570 | 750 | 436 | 314 | 172 | 7.1 | 125 | 0 | 0.2 | 871 | 107
2015-06-21 | 7.58 | 18 | 0.5 | 1490 | 672 | 445 | 227 | 189 | 7.3 | 120 | 0 | 0.2 | 866 | 108
2015-06-22 | 7.55 | 20 | 0.4 | 1660 | 652 | 444 | 208 | 215 | 7.6 | 115 | 0 | 0.2 | 878 | 107
2015-06-23 | 7.7 | 19 | 0.2 | 1630 | 652 | 445 | 208 | 189 | 7.5 | 120 | 0 | 0.2 | 866 | 105
2015-06-24 | 7.6 | 18 | 0.2 | 1480 | 656 | 448 | 208 | 197 | 7.4 | 125 | 0 | 0.2 | 875 | 108
2015-06-25 | 7.86 | 19 | 0.1 | 1540 | 592 | 324 | 268 | 198 | 7.1 | 110 | 0 | 0.2 | 868 | 107
2015-06-26 | 7.55 | 18 | 0.3 | 1455 | 608 | 352 | 256 | 198 | 7 | 115 | 0 | 0.2 | 870 | 110
2015-06-27 | 7.6 | 18 | 0.3 | 1470 | 564 | 324 | 240 | 206 | 7.5 | 120 | 0 | 0.2 | 874 | 112
2015-06-28 | 7.58 | 16 | 0.3 | 1520 | 600 | 360 | 240 | 215 | 7.6 | 120 | 0 | 0.2 | 868 | 115
2015-06-29 | 7.7 | 16 | 0.2 | 1550 | 608 | 352 | 256 | 206 | 7.5 | 120 | 0 | 0.2 | 870 | 112
2015-06-30 | 7.85 | 17 | 0.2 | 1620 | 616 | 340 | 276 | 240 | 7.2 | 115 | 0 | 0.2 | 878 | 110
MIN. | 7.4 | 15 | 0 | 1289 | 580 | 324 | 208 | 120 | 7 | 100 | 0 | 0.2 | 719 | 98
MAX. | 7.86 | 20 | 0.5 | 1800 | 872 | 540 | 332 | 386 | 7.9 | 130 | 0 | 0.2 | 880 | 115
No. of < Spec | 1 | -- | 13 | -- | -- |  | -- | -- | 0 | -- | - | -- | -- | --
No. of > Spec | 0 | 0 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | 0 | 0
% < Specs. | 3.3333 | -- | 46.4286 | -- | -- | -- | -- | -- | 0 |  |  |  |  | --
% > Specs. | 0 | 0 | 0 | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 | 0 | 0