## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | Max. 1000 ppm | 180 ppm
01.07.15 | 7.6 | 16 | 0.2 | 1510 | 612 | 348 | 264 | 348 | 7.3 | 122 | 0 | 0.2 | 870 | 115
02.07.15 | 7.7 | 18 | 0.2 | 1510 | 628 | 356 | 272 | 356 | 7.2 | 124 | 0 | 0.2 | 852 | 112
03.07.15 | 7.7 | 18 | 0.2 | 1510 | 592 | 324 | 268 | 324 | 7 | 145 | 0 | 0.2 | 870 | 110
04.07.15 | 7.5 | 18 | 0.1 | 1540 | 676 | 380 | 296 | 380 | 7.2 | 148 | 0 | 0.2 | 852 | 115
05.07.15 | 7.5 | 17 | 0.1 | 1550 | 636 | 360 | 276 | 360 | 7 | 152 | 0 | 0.2 | 865 | 110
06.07.15 | 7.7 | 17 | 0.1 | 1535 | 656 | 372 | 284 | 372 | 7.1 | 155 | 0 | 0.2 | 855 | 115
07.07.15 | 7.5 | 17 | 0.2 | 1475 | 600 | 336 | 264 | 336 | 7.1 | 160 | 0 | 0.2 | 810 | 115
08.07.15 | 7.7 | 18 | 0.1 | 1505 | 652 | 324 | 328 | 324 | 7.2 | 155 | 0 | 0.2 | 822 | 112
09.07.15 | 7.6 | 17 | 0.1 | 1450 | 648 | 364 | 284 | 364 | 7.2 | 152 | 0 | 0.2 | 823 | 115
10.07.15 | 7.7 | 17 | 0.2 | 1500 | 620 | 352 | 268 | 352 | 7.3 | 158 | 0 | 0.2 | 829 | 110
11.07.15 | 7.7 | 18 | 0.2 | 1450 | 612 | 360 | 252 | 360 | 7.1 | 160 | 0 | 0.2 | 825 | 115
12.07.15 | 7.8 | 17 | 0.1 | 1420 | 600 | 336 | 264 | 336 | 7.1 | 158 | 0 | 0.2 | 832 | 110
13.07.15 | 7.7 | 18 | 0.1 | 1400 | 592 | 348 | 244 | 348 | 7.3 | 160 | 0 | 0.2 | 840 | 115
14.07.15 | 7.6 | 17 | 0.2 | 1480 | 604 | 348 | 256 | 348 | 7.3 | 165 | 0 | 0.2 | 865 | 115
15.07.15 | 7.7 | 17 | 0.2 | 1460 | 612 | 364 | 248 | 364 | 7.6 | 160 | 0 | 0.2 | 854 | 116
16.07.15 | 7.9 | 17 | 0.2 | 1450 | 616 | 388 | 228 | 388 | 6.8 | 162 | 0 | 0.2 | 850 | 116
17.07.15 | 7.8 | 18 | 0.1 | 1435 | 604 | 368 | 236 | 368 | 6.8 | 165 | 0 | 0.2 | 839 | 114
18.07.15 | 7.7 | 17 | 0.2 | 1460 | 634 | 391 | 243 | 391 | 6.9 | 160 | 0 | 0.2 | 845 | 112
19.07.15 | 7.6 | 15 | 0.1 | 1410 | 624 | 368 | 256 | 368 | 7.2 | 156 | 0 | 0.2 | 860 | 1110
20.07.15 | 7.7 | 16 | 0.2 | 1390 | 624 | 380 | 244 | 380 | 7 | 158 | 0 | 0.2 | 865 | 112
21.07.15 | 7.5 | 17 | 0.2 | 1410 | 556 | 340 | 216 | 340 | 6.7 | 160 | 0 | 0.2 | 860 | 110
22.07.15 | 7.9 | 17 | 0.2 | 1405 | 588 | 384 | 204 | 384 | 6.8 | 162 | 0 | 0.2 | 865 | 115
23.07.15 | 7.7 | 18 | 0.1 | 1415 | 536 | 340 | 196 | 340 | 6.7 | 1580 | 0 | 0.2 | 860 | 110
24.07.15 | 7.8 | 17 | 0.1 | 1470 | 536 | 336 | 200 | 336 | 6.9 | 160 | 0 | 0.2 | 865 | 115
25.07.15 | 7.5 | 17 | 0.1 | 1460 | 556 | 340 | 216 | 340 | 6.8 | 158 | 0 | 0.2 | 860 | 112
26.07.15 | 7.6 | 16 | 0.2 | 1510 | 548 | 348 | 200 | 348 | 6.7 | 160 | 0 | 0.2 | 830 | 113
27.07.15 | 7.5 | 17 | 0.1 | 1520 | 556 | 336 | 220 | 336 | 7.1 | 162 | 0 | 0.2 | 876 | 115
28.07.15 | 7.7 | 17 | 0.1 | 1490 | 524 | 320 | 204 | 320 | 7 | 164 | 0 | 0.2 | 859 | 112
29.07.15 | 7.8 | 17 | 0.1 | 1595 | 532 | 324 | 208 | 324 | 7.2 | 160 | 0 | 0.2 | 850 | 110
30.07.15 | 7.8 | 17 | 0.1 | 1645 | 520 | 328 | 192 | 328 | 6.5 | 160 | 0 | 0.2 | 831 | 112
31.07.15 | 7.7 | 17 | 0.1 | 1490 | 536 | 344 | 192 | 344 | 6.6 | 162 | 0 | 0.2 | 840 | 113
MIN. | 7.5 | 15 | 0.1 | 1390 | 520 | 320 | 192 | 320 | 4.8 | 122 | 0 | 0.2 | 859 | 110
MAX. | 7.9 | 18 | 0.2 | 1645 | 676 | 391 | 328 | 391 | 4.6 | 1580 | 0 | 0.2 | 876 | 1110
No. of < Spec | 0 | -- | 16 | -- | -- |  | -- | -- | 0 | -- | - | - | -- | --
No. of > Spec | 0 | 0 | 0 | 0 | 0 | -- | -- | 0 | 0 | 1 | -- | 0 | 0 | 1
% < Specs. | 0 | -- | 53.3333 | -- | -- | -- | -- | -- | 0 |  |  |  |  | --
% > Specs. | 0 | 0 | 0 | 0 | 0 |  | -- | 0 | 0 | 3.3333 |  | 0 | 0 | 3.3333