## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
03.03.24 | 8.3 | - | - | 328 | 220 | 136 | 89 | 47 | 36 | 1.8 | - | NIL | 0.2 |  |  | 3.2
05.03.24 | 8.92 | 66 | NIL | 354 | 237 | 148 | 68 | 80 | 14 | - | - | NIL | - |  |  | 5
06.03.24 | 8.48 | 47 | NIL | 335 | 225 | 154 | 84 | 70 | 18 | - | - | NIL | - |  |  | 5
09.03.24 | 8.57 | 35 | NIL | 362 | 243 | 114 | 76 | 38 | 30 | 2 | - | NIL | - |  |  | 4.1
10.03.24 | 8.59 | 29 | NIL | 377 | 253 | 127 | 76 | 51 | 36 | 1.7 | - | NIL | - |  |  | 4
11.03.24 | 8.51 | 19 | NIL | 418 | 280 | 131 | 79 | 52 | 36 | 2.2 | - | NIL | - |  |  | 4.3
12.03.24 | 8.48 | 19 | NIL | 415 | 278 | 142 | 85 | 57 | 33 | 2.3 | - | NIL | - |  |  | 4.6
13.03.24 | 8.42 | 21 | NIL | 423 | 284 | 148 | 89 | 59 | 36 | 2.5 | - | NIL | - |  |  | 4.4
14.03.24 | 8.39 | 24 | NIL | 428 | 287 | 147 | 85 | 62 | 33 | 2.4 | - | NIL | - |  |  | 4.3
15.03.24 | 8.64 | 28 | NIL | 443 | 297 | 179 | 94 | 85 | 29 | 1.8 | - | NIL | - |  |  | 4.1
16.03.24 | 8.63 | 25 | NIL | 411 | 276 |  |  | 0 |  |  | - | NIL
18.03.24 | 8.75 | 12 | NIL | 415 | 278 | 152 | 94 | 58 | 36 | - | - | NIL | -
20.03.24 | 8.59 | 19 | NIL | 388 | 260 | 205 | 127 | 78 | 28 | 3.4 | - | NIL | - |  |  | 9
21.03.24 | 8.67 | 15 | NIL | 447 | 300 | 192 | 119 | 73 | 31 | - | - | NIL | -
22.03.24 | 8.41 | 4 | NIL | 321 | 215 | 223 | 123 | 100 | 36 | - | - | NIL | - |  |  | 9
23.03.24 | 8.62 | 4 | NIL | 432 | 290 | 114 | 105 | 9 | 43 | - | - | NIL |  |  |  | 8
26.03.24 | 8.59 | 4 | NIL | 358 | 240 | 146 | 100 | 46 | 32 | - | - | NIL
27.03.24 | 8.6 | 4 | NIL | 449 | 301 | 205 | 132 | 73 | 36 | - | - | NIL |  |  |  | 10
28.03.24 | 8.47 | 10 | NIL | 464 | 311 | 228 | 141 | 87 | 29 | - | - | NIL |  |  |  | 8
29.03.24 | 8.44 | 10 | NIL | 464 | 311 | 210 | 119 | 91 | 36 | - | - | NIL |  |  |  | 10
30.03.24 | 8.32 | 11 | NIL | 562 | 377 | 219 | 105 | 114 | 29 | - | - | NIL |  |  |  | 12
[11 empty] | - | NIL
[11 empty] | - | NIL
| 8.3 | 17 | 0 | 321 | 215 | 114 | 68 | 0 | 142 | 5.8 | 0 | 0 | 0 | 0 | 0 | 3.2
MAX. | 8.92 | 28 | 0 | 562 | 377 | 228 | 141 | 114 | 142 | 10.5 | 0 | 0 | 0 | 0 | 0 | 12
AVG. | 8.5424 | 19 |  | 409.2381 | 274.4286 | 166 | 99.5 | 63.3333 | 37.0952 | 2.2333 |  | 0 |  |  |  | 6.4118
No. of < Spec | 0 | -- | 0 | -- | -- | -- | -- | -- | -- | 9 | -- | -- | -- | -- | -- | --
No. of > Spec | 21 | 8 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- |  | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 100 | 40 |  |  | 0 | 0 |  | -- | 0 | 0 | [5 empty] | 0