## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.01.22 | 8.2 | 31 | 0.4 | 2301 | 1542 | 726 | 498 | 228 | 226 | 7 | 125 | NIL | 0.2 | 31 | 874 | 153
02.01.22 | 8.2 | 29 | 0.3 | 2358 | 1580 | 730 | 448 | 282 | 228 | 7.1 | 123 | NIL | 0.3 | 29 | 754 | 157
03.01.22 | 8.2 | 29 | 0.3 | 2358 | 1580 | 730 | 448 | 282 | 228 | 7.1 | 123 | NIL | 0.3 | 29 | 754 | 157
04.01.22 | 8.5 | 26 | 0.2 | 2149 | 1440 | 743 | 467 | 276 | 253 | 6.4 | 139 | NIL | 0.2 | 26 | 893 | 162
05.01.22 | 8.5 | 33 | 0.1 | 2104 | 1410 | 795 | 510 | 285 | 214 | 6.8 | 133 | NIL | 0.2 | 33 | 878 | 169
06.01.22 | 8.5 | 24 | 0 | 2036 | 1364 | 786 | 501 | 285 | 222 | 6.9 | 139 | NIL | 0.2 | 24 | 890 | 156
07.01.22 | 8.1 | 22 | 0 | 2015 | 1350 | 752 | 483 | 269 | 212 | 7 | 120 | NIL | 0.2 | 22 | 927 | 149
08.01.22 | 8.1 | 18 | 0 | 2127 | 1427 | 769 | 500 | 269 | 202 | 7.1 | 124 | NIL | 0.2 | 18 | 911 | 162
09.01.22 | 8.4 | 23 | 0 | 2394 | 1540 | 960 | 592 | 368 | 216 | 6.6 | 133 | NIL | 0.2 | 23 | 873 | 174
10.01.22 | 8.4 | 18 | 0 | 2073 | 1389 | 727 | 504 | 223 | 216 | 6.1 | 139 | NIL | 0.2 | 18 | 893 | 150
11.01.22 | 8.5 | 20 | 0 | 2213 | 1483 | 764 | 487 | 277 | 209 | 6.6 | 135 | NIL | 0.2 | 20 | 754 | 162
12.01.22 | 8.5 | 24 | 0 | 2257 | 1570 | 798 | 500 | 298 | 198 | 6.2 | 132 | NIL | 0.2 | 24 | 894 | 156
13.01.22 | 8.2 | 16 | 0 | 2000 | 1340 | 748 | 508 | 240 | 187 | 6.5 | 129 | NIL | 0.2 | 16 | 890 | 160
15.01.22 | 8.3 | 18 | 0 | 1984 | 1332 | 733 | 492 | 241 | 182 | 6.2 | 122 | NIL | 0.2 | 18 | 899 | 156
16.01.22 | 8.2 | 19 | 0 | 1955 | 1310 | 777 | 479 | 298 | 210 | 6 | 124 | NIL | 0.2 | 19 | 878 | 156
17.01.22 | 8.5 | 18 | 0 | 2179 | 1460 | 802 | 496 | 306 | 187 | 6 | 124 | NIL | 0.2 | 18 | 916 | 149
[12 empty] | NIL |  |  | 910
20.01.22 | 8.1 | 20 | 0 | 2284 | 1530 | 798 | 525 | 273 | 180 | 6 | 124 | NIL | 0.2 | 20 | 910 | 158
21.01.22 | 8 | 16 | 0 | 2600 | 1560 | 777 | 500 | 277 | 184 | 6.2 | 120 | NIL | 0.2 | 16 | 873 | 162
22.01.22 | 8.2 | 15 | 0 | 2208 | 1480 | 756 | 517 | 198 | 198 | 6.3 | 124 | NIL | 0.2 | 15 | 875 | 150
23.01.22 | 8.2 | 36 | 0 | 2313 | 1550 | 781 | 462 | 319 | 218 | 6.1 | 130 | NIL | 0.2 | 36 | 888 | 167
24.01.22 | 8.3 | 18 | 0 | 2284 | 1502 | 770 | 524 | 246 | 202 | 6.4 | 120 | NIL | 0.2 | 18 | 878 | 152
25.01.22 | 8.2 | 32 | 0.5 | 2328 | 1560 | 790 | 540 | 250 | 210 | 5.9 | 123 | NIL | 0.2 | 32 | 916 | 164
27.01.22 | 8.4 | 39 | 0.7 | 2194 | 1470 | 811 | 572 | 239 | 184 | 6.3 | 130 | NIL | 0.2 | 39 | 910 | 162
28.01.22 | 8.1 | 31 | 0 | 2242 | 1580 | 806 | 554 | 252 | 191 | 6.2 | 128 | NIL | 0.2 | 31 | 873 | 165
29.01.22 | 8.3 | 32 | 0.1 | 2350 | 1570 | 819 | 538 | 281 | 194 | 6 | 133 | NIL | 0.2 | 32 | 875 | 156
30.01.22 | 8 | 24 | 0.1 | 2513 | 1634 | 730 | 422 | 308 | 210 | 6.9 | 122 | NIL | 0.2 | 24 | 888 | 153
31.01.22 | 8.1 | 32 | 0 | 2253 | 1598 | 872 | 560 | 312 | 202 | 6 | 127 | NIL | 0.2 | 32 | 888 | 160
MIN. | 8 | 17 | 0 | 1955 | 1310 | 726 | 422 | 198 | 142 | 5.8 | 120 | 0 | 0.2 | 15 | 754 | 149
MAX. | 8.5 | 28 | 0.7 | 2600 | 1634 | 960 | 592 | 368 | 253 | 10.5 | 139 | 0 | 0.3 | 39 | 927 | 174
AVG. | 8.2667 | 19 | 0.1 | 2224.8889 | 1487.0741 | 779.6296 | 504.7037 | 273.4074 | 203.75 | 6.4407 | 127.5926 | 0 | 0.20769 | 24.5556 | 877.2143 | 158.4074
No. of < Spec | 0 | -- | 21 | -- | -- | -- | -- | -- | -- | 1 | -- | -- | -- | -- | -- | --
No. of > Spec | 25 | 16 | 1 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- | 77.7778 | -- | -- | -- | -- | -- | -- | 3.7037 | [5 empty] | --
% > Specs. | 92.5926 | 59.2593 | 3.7037 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0