## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.03.24 |  | 100 |  | 2123 | 1423 | [6 empty] | NIL | 0.5
02.03.24 | 7.47 | 109 | NIL | 2349 | 1574 | 1001 | 589 | 412 | 252 | 4.8 | - | NIL | 0.5 |  |  | 63
04.03.24 | 7.56 | 76 | NIL | 2223 | 1490 | 996 | 538 | 458 | 259 | 4.7 | - | NIL | 0.5 |  |  | 60
05.03.24 | 7.71 | 87 | NIL | 2254 | 1510 | 979 | 526 | 453 | 267 | 4.8 | - | NIL | 0.5 |  |  | 61
06.03.24 | 7.65 | 62 | NIL | 2218 | 1486 | 971 | 513 | 458 | 252 | 4.3 | - | NIL | 0.5 |  |  | 58
2024-03-07 | 7.43 | 59 | NIL | 2394 | 1604 | 954 | 517 | 437 | 231 | 4.1 | - | NIL | 0.5 |  |  | 50
09.03.24 | 7.52 | 48 | NIL | 2363 | 1583 | 933 | 479 | 454 | 223 | 4.1 | - | NIL | 0.5 |  |  | 59
11.03.24 | 7.14 | 60 | NIL | 2820 | 1890 | 988 | 526 | 462 | 238 | 4.3 | - | NIL | 0.5 |  |  | 61
2024-03-12 | 7.88 | 67 | NIL | 2761 | 1850 | 979 | 513 | 466 | 223 | 4.1 | - | NIL | 0.5 |  |  | 56
2024-03-13 | 7.63 | 71 | NIL | 2754 | 1845 | 992 | 511 | 481 | 231 | 4.2 | - | NIL | 0.5 |  |  | 59
2024-03-14 | 8.13 | 60 | NIL | 2555 | 1712 | 967 | 521 | 446 | 245 | 4 | - | NIL | 0.5 |  |  | 56
15.03.24 | 8.08 | 61 | NIL | 2619 | 1755 | 1007 | 560 | 447 | 223 | 4.6 | - | NIL | 0.5 |  |  | 63
2024-03-18 | 8.12 | 44 | NIL | 2253 | 1510 | 883 | 496 | 387 | 231 | 4.5 | - | NIL | 0.5 |  |  | 59
2024-03-19 | 8.23 | 39 | NIL | 2223 | 1490 | 803 | 483 | 320 | 223 | 4.3 | - | NIL | 0.5 |  |  | 58
20.03.24 | 7.66 | 39 | NIL | 2051 | 1374 | 812 | 488 | 324 | 231 | 4.2 | - | NIL | 0.5 |  |  | 58
2024-03-21 | 7.41 | 30 | NIL | 2156 | 1445 | 798 | 492 | 306 | 238 | 4.1 | - | NIL | 0.5 |  |  | 58
2024-03-22 | 7.96 | 35 | NIL | 2088 | 1399 | 766 | 447 | 319 | 223 | 3.8 | - | NIL | 0.4 |  |  | 51
2024-03-23 | 8.37 | 26 | NIL | 1958 | 1312 | 780 | 461 | 319 | 209 | 3.2 | - | NIL | 0.5 |  |  | 50
2024-03-26 | 7.89 | 31 | NIL | 2166 | 1451 | 876 | 543 | 333 | 218 | 3.4 | - | NIL | 0.5 |  |  | 51
2024-03-27 | 7.75 | 30 | NIL | 2087 | 1398 | 866 | 547 | 319 | 233 | 3.5 | - | NIL | 0.5 |  |  | 54
2024-03-28 | 8.26 | 23 | NIL | 1976 | 1324 | 873 | 538 | 335 | 225 | 3.2 | - | NIL | 0.5 |  |  | 56
2024-03-29 | 8.21 | 21 | NIL | 2164 | 1450 | 921 | 561 | 360 | 211 | 2.6 | - | NIL | 0.6 |  |  | 65
2024-03-30 | 7.55 | 28 | NIL | 2279 | 1527 | 948 | 588 | 360 | 204 | 2.5 | - | NIL | 0.6 |  |  | 73
MIN. | 7.14 | 17 | 0 | 1958 | 1312 | 766 | 447 | 306 | 142 | 5.8 | 0 | 0 | 0.4 | 0 | 0 | 50
MAX. | 8.37 | 28 | 0 | 2820 | 1890 | 1007 | 589 | 481 | 267 | 10.5 | 0 | 0 | 0.6 | 0 | 0 | 73
AVG. | 7.8005 | 19 |  | 2297.1304 | 1539.2174 | 913.3182 | 519.8636 | 393.4545 | 227.4783 | 3.9682 |  | 0 | 0.50455 |  |  | 58.1364
No. of < Spec | 4 | -- | 0 | -- | -- | -- | -- | -- | -- | 22 | -- | -- | -- | -- | -- | --
No. of > Spec | 7 | 23 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 18.1818 | -- |  | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 31.8182 | 100 |  |  | 0 | 0 |  | -- | 0 | 0 |  |  | 0 |  |  | 0