## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.08.23 | 7.5 | 19 | 0.1 | 1495 | 1000 | 604 | 330 | 274 | 290 | 6.2 | 93 | NIL | 0.4 | 19 | 874 | 124
02.05.23 | 7.6 | 22 | 0 | 1896 | 1270 | 588 | 340 | 248 | 229 | 6.7 | 113 | NIL | 0.3 | 22 | 893 | 123
03.05.23 | 7.8 | 23 | 0.2 | 1836 | 1230 | 580 | 332 | 204 | 244 | 6.9 | 112 | NIL | 0.4 | 23 | 754 | 130
04.08.23 | 7 | 22 | 0.7 | 1632 | 1094 | 613 | 307 | 306 | 272 | 6.4 | 82 | NIL | 0.5 | 22 | 901 | 120
05.08.23 | 7.7 | 18 | 0.1 | 1855 | 1230 | 632 | 353 | 279 | 252 | 6 | 105 | NIL | 0.5 | 18 | 901 | 116
06.05.23 | 7.6 | 14 | 0.2 | 1683 | 1128 | 623 | 371 | 252 | 213 | 6.4 | 110 | NIL | 0.4 | 14 | 883 | 116
07.08.23 | 7.8 | 18 | 0.1 | 1851 | 1240 | 632 | 354 | 278 | 252 | 6 | 100 | NIL | 0.5 | 18 | 890 | 116
08.08.23 | 7.7 | 17 | 0 | 1882 | 1250 | 620 | 340 | 280 | 248 | 6.2 | 98 | NIL | 0.5 | 17 | 893 | 110
09.08.23 | 7.4 | 14 | 0.6 | 1896 | 1270 | 603 | 349 | 254 | 343 | 6.9 | 102 | NIL | 0.5 | 14 | 754 | 128
10.08.23 | 7.4 | 13 | 0 | 1701 | 1140 | 595 | 341 | 254 | 342 | 7.3 | 104 | NIL | 0.5 | 13 | 885 | 133
11.08.23 | 7.6 | 16 | 0 | 1690 | 1120 | 590 | 355 | 235 | 340 | 7 | 100 | NIL | 0.5 | 16 | 881 | 130
12.08.23 | 7.8 | 14 | 0 | 1835 | 1230 | 507 | 329 | 178 | 321 | 6.6 | 116 | NIL | 5 | 14 | 890 | 123
| 8 | 34 | 0 | 1436 | 962 | 610 | 436 | 174 | 216 | 6.3 | 114 | NIL | 0.4 | 34 | 894 | 129
14.08.23 | 7.8 | 12 | 0.1 | 1791 | 1200 | 618 | 335 | 283 | 326 | 5 | 109 | NIL | 0.5 | 12 | 899 | 120
15.08.23 | 7.7 | 13 | 0.1 | 1820 | 1240 | 600 | 320 | 280 | 320 | 6.2 | 100 | NIL | 0.4 | 13 | 878 | 116
16.08.23 | 7.2 | 27 | 0.1 | 1522 | 1020 | 623 | 359 | 264 | 332 | 6.4 | 114 | NIL | 0.5 | 27 | 916 | 119
17.08.23 | 7.3 | 20 | 0 | 1572 | 1053 | 640 | 369 | 271 | 340 | 6.7 | 100 | NIL | 0.4 | 20 | 929 | 122
18.08.23 | 7.7 | 18 | 0.1 | 1734 | 1162 | 632 | 324 | 308 | 321 | 7.5 | 110 | NIL | 0.5 | 18 | 870 | 124
19.08.23 | 7.3 | 16 | 0.1 | 1555 | 1042 | 624 | 316 | 307 | 307 | 7.1 | 100 | NIL | 0.5 | 16 | 879 | 120
20.05.23 | 7.7 | 32 | 0.4 | 1487 | 996 | 506 | 314 | 198 | 209 | 6.6 | 109 | NIL | 0.4 | 32 | 875 | 126
21.05.23 | 8.1 | 18 | 0.2 | 1448 | 970 | 480 | 301 | 179 | 216 | 5.9 | 122 | NIL | 0.4 | 18 | 888 | 113
22.05.23 | 7.7 | 33 | 0.6 | 1478 | 990 | 449 | 281 | 168 | 213 | 6 | 118 | NIL | 0.2 | 33 | 878 | 110
23.05.23 | 8.1 | 19 | 0.1 | 1473 | 987 | 514 | 323 | 191 | 230 | 6.6 | 119 | NIL | 0.4 | 19 | 881 | 118
24.05.23 | 8 | 16 | 0.3 | 1332 | 893 | 501 | 314 | 187 | 223 | 6.4 | 119 | NIL | 0.4 | 16 | 882 | 110
25.08.23 | 7.7 | 30 | 0 | 1701 | 1140 | 659 | 408 | 251 | 358 | 7 | 100 | NIL | 0.5 | 30 | 892 | 118
26.05.23 | 7.9 | 14 | 0 | 1334 | 894 | 514 | 340 | 174 | 209 | 6.5 | 116 | NIL | 0.4 | 14 | 890 | 112
27.05.23 | 7.7 | 22 | 0.5 | 1388 | 930 | 506 | 331 | 175 | 202 | 7 | 114 | NIL | 0.4 | 22 | 887 | 120
28.05.23 | 7.7 | 22 | 0.5 | 1388 | 930 | 506 | 331 | 175 | 202 | 7 | 114 | NIL | 0.4 | 22 | 891 | 120
29.08.23 | 7.8 | 11 | 0.6 | 1385 | 928 | 613 | 349 | 264 | 347 | 5.4 | 110 | NIL | 0.5 | 11 | 910 | 132
30.05.23 | 7.8 | 22 | 0.5 | 1254 | 840 | 471 | 292 | 179 | 202 | 6 | 110 | NIL | 0.4 | 22 | 873 | 112
31.08.23 | 7.4 | 14 | 0.2 | 1597 | 1070 | 516 | 357 | 159 | 320 | 6.4 | 102 | 0.5 | 0.5 | 14 | 875 | 124
MIN. | 7 | 17 | 0 | 1254 | 840 | 449 | 281 | 159 | 142 | 5.8 | 82 | 0.5 | 0.2 | 11 | 754 | 110
MAX. | 8.1 | 28 | 0.7 | 1896 | 1270 | 659 | 436 | 308 | 358 | 10.5 | 122 | 0.5 | 5 | 34 | 929 | 133
AVG. | 7.6613 | 19 | 0.20645 | 1611.1935 | 1079 | 573.1935 | 338.7419 | 233.1935 | 268.1562 | 6.471 | 107.5806 | 0 | 0.59 | 19.4516 | 880.1935 | 120.4516
No. of < Spec | 7 | -- | 18 | -- | -- | -- | -- | -- | -- | 3 | -- | -- | -- | -- | -- | --
No. of > Spec | 2 | 11 | 4 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 1 | -- | 0 | 0
% < Specs. | 22.5806 | -- | 58.0645 | -- | -- | -- | -- | -- | -- | 9.6774 | [5 empty] | --
% > Specs. | 6.4516 | 35.4839 | 12.9032 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 3.3333 |  | 0 | 0