## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2023-12-01 | 8.77 | 64 | NIL | 1739 | 1165 | 845 | 392 | 453 | 275 | 3.1 | - | NIL | 0.5 |  |  | 61
2023-12-02 | 8.61 | 45 | NIL | 1858 | 1245 | 906 | 444 | 462 | 296 | 2.8 | - | NIL | 0.5 |  |  | 57
2023-12-04 | 8.22 | 43 | NIL | 1850 | 1240 | 884 | 466 | 418 | 282 | 3 | - | NIL | 0.5 |  |  | 66
2023-12-06 | 8.24 | 30 | NIL | 1805 | 1210 | 889 | 475 | 414 | 289 | 3 | - | NIL | 0.5 |  |  | 49
2023-12-14 | 7.27 | 24 | NIL | 1546 | 1036 | 862 | 506 | 356 | 274 | 3.7 | - | NIL | 0.5 |  |  | 89
2023-12-15 | 7.19 | 53 | NIL | 1685 | 1129 | 876 | 537 | 339 | 303 | 3.9 | - | NIL | 0.5 |  |  | 91
2023-12-16 | 5.72 | 60 | NIL | 1910 | 1230 | 867 | 528 | 339 | 289 | 4 | - | NIL | 0.5 |  |  | 90
2023-12-18 | 7.42 | 51 | NIL | 1568 | 1051 | 871 | 532 | 339 | 244 | 3.9 | - | NIL | 0.5 |  |  | 86
2023-12-20 | 8.1 | 43 | NIL | 1409 | 944 | 980 | 607 | 373 | 244 | 4 | - | NIL | 0.5 |  |  | 82
2023-12-21 | 7.88 | 45 | NIL | 1314 | 881 | 957 | 598 | 359 | 252 | 4.2 | - | NIL | 0.5 |  |  | 89
2023-12-22 | 8.2 | 44 | NIL | 1256 | 842 | 966 | 584 | 382 | 274 | 3.8 | - | NIL | 0.5 |  |  | 82
2023-12-23 | 7.8 | 35 | NIL | 1294 | 837 | 998 | 609 | 389 | 252 | 3.5 | - | NIL | 0.5 |  |  | 79
2023-12-25 | 7.8 | 49 | NIL | 1294 | 867 | 994 | 589 | 405 | 244 | 3.5 | - | NIL | 0.5 |  |  | 78
2023-12-26 | 8.17 | 49 | NIL | 1476 | 989 | 975 | 580 | 395 | 266 | 3.9 | - | NIL | 0.5 |  |  | 86
2023-12-27 | 8.44 | 42 | NIL | 1441 | 966 | 944 | 469 | 475 | 237 | 2.5 | - | NIL | 0.5 |  |  | 83
2023-12-28 | 7.78 | 34 | NIL | 1358 | 910 | 897 | 460 | 437 | 229 | 1.7 | - | NIL | 0.5 |  |  | 89
2023-12-29 | 7.5 | 33 | 0.8 | 1349 | 904 | 874 | 474 | 400 | 244 | 1.4 | - | NIL | 0.5 |  |  | 85
2023-12-30 | 7.95 | 32 | 0.8 | 1194 | 800 | 901 | 510 | 391 | 221 | 60 | - | NIL | 0.5 |  |  | 60
[11 empty] | - | NIL
[11 empty] | - | NIL
[8 empty] | 0 |  |  |  | NIL
MIN. | 5.72 | 17 | 0.8 | 1194 | 800 | 845 | 392 | 0 | 142 | 5.8 | 0 | 0 | 0.5 | 0 | 0 | 49
MAX. | 8.77 | 28 | 0.8 | 1910 | 1245 | 998 | 609 | 475 | 303 | 10.5 | 0 | 0 | 0.5 | 0 | 0 | 91
AVG. | 7.8367 | 19 | 0.8 | 1519.2222 | 1013.6667 | 915.8889 | 520 | 375.0526 | 255.6316 | 6.4389 |  | 0 | 0.5 |  |  | 77.8889
No. of < Spec | 4 | -- | 0 | -- | -- | -- | -- | -- | -- | 17 | -- | -- | -- | -- | -- | --
No. of > Spec | 8 | 18 | 2 | -- | 0 | 0 | -- | -- | 0 | 1 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 22.2222 | -- | 0 | -- | -- | -- | -- | -- | -- | 94.4444 | [5 empty] | --
% > Specs. | 44.4444 | 100 | 100 |  | 0 | 0 |  | -- | 0 | 5.5556 |  |  | 0 |  |  | 0