## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2024-02-01 |  | 43 | NIL | 2185 | 1464 | 767 | 360 | 407 | 192 | 3.7 | - | NIL | 0.5 |  |  | 65
2024-02-02 | 7.15 | 43 | 0.4 | 2246 | 1505 | 789 | 377 | 412 | 178 | 3.8 | - | NIL | 0.5 |  |  | 66
2024-02-03 | 7.2 | 61 | NIL | 2280 | 1528 | 827 | 437 | 390 | 170 | 3.2 | - | NIL | 0.5 |  |  | 58
2024-02-05 | 7.69 | 61 | NIL | 2248 | 1506 | 801 | 424 | 377 | 170 | 3.4 | - | NIL | 0.5 |  |  | 69
2024-02-06 | 7.57 | 11 | NIL | 1690 | 1132 | 810 | 445 | 365 | 155 | 3.9 | - | NIL | 0.5 |  |  | 61
2024-02-07 | 7.69 | 62 | NIL | 2413 | 1617 | 831 | 488 | 343 | 185 | 3.3 | - | NIL | 0.5 |  |  | 58
2024-02-08 | 7.69 | 59 | NIL | 2185 | 1464 | 755 | 424 | 331 | 178 | 3.4 | - | NIL | 0.5 |  |  | 61
2024-02-09 | 7.33 | 61 | NIL | 2219 | 1487 | 784 | 458 | 326 | 207 | 3.1 | - | NIL | 0.5 |  |  | 57
2024-02-10 | 7.61 | 58 | NIL | 2376 | 1592 | 734 | 479 | 255 | 237 | 2.9 | - | NIL | 0.5 |  |  | 59
2024-02-12 | 7.94 | 75 | NIL | 2422 | 1623 | 776 | 445 | 331 | 259 | 3.3 | - | NIL | 0.5 |  |  | 59
2024-02-13 | 7.96 | 55 | NIL | 2397 | 1606 | 831 | 466 | 365 | 281 | 3.2 | - | NIL | 0.5 |  |  | 66
2024-02-14 | 7.8 | 55 | NIL | 2264 | 1517 | 797 | 432 | 365 | 252 | 2.9 | - | NIL | 0.5 |  |  | 63
2024-02-15 | 8.14 | 34 | NIL | 2152 | 1442 | 806 | 424 | 382 | 237 | 3.1 | - | NIL | 0.5 |  |  | 60
2024-02-16 | 8.18 | 35 | NIL | 2343 | 1570 | 852 | 437 | 415 | 259 | 2.8 | - | NIL | 0.5 |  |  | 58
2024-02-20 | 7.41 | 75 | NIL | 2897 | 1941 | 929 | 492 | 437 | 244 | 3.1 | - | NIL | 0.5 |  |  | 61
2024-02-21 | 7.41 | 78 | NIL | 2373 | 1590 | 903 | 479 | 424 | 252 | 3.6 | - | NIL | 0.5 |  |  | 59
2024-02-22 | 8.05 | 51 | NIL | 2379 | 1594 | 916 | 488 | 428 | 237 | 3.4 | - | NIL | 0.5 |  |  | 53
2024-02-23 | 7.73 | 37 | NIL | 2178 | 1459 | 873 | 500 | 373 | 259 | 3.5 | - | NIL | 0.5 |  |  | 57
2024-02-26 | 7.89 | 76 | NIL | 2215 | 1484 | 929 | 492 | 437 | 259 | 4.1 | - | NIL | 0.5 |  |  | 58
2024-02-27 | 7.42 | 46 | NIL | 2164 | 1450 | 954 | 522 | 432 | 281 | 4.2 | - | NIL | 0.5 |  |  | 63
2024-02-28 | 8.09 | 93 | NIL | 2068 | 1389 | 920 | 500 | 420 | 244 | 4 | - | NIL | 0.5 |  |  | 55
2024-02-29 | 7.92 | 92 | NIL | 2066 | 1384 | 924 | 492 | 432 | 252 | 4.3 | - | NIL | 0.5 |  |  | 61
[8 empty] | 0 |  |  |  | NIL
MIN. | 7.15 | 17 | 0.4 | 1690 | 1132 | 734 | 360 | 0 | 142 | 5.8 | 0 | 0 | 0.5 | 0 | 0 | 53
MAX. | 8.18 | 28 | 0.4 | 2897 | 1941 | 954 | 522 | 437 | 281 | 10.5 | 0 | 0 | 0.5 | 0 | 0 | 69
AVG. | 7.7081 | 19 | 0.4 | 2261.8182 | 1515.6364 | 841.2727 | 457.3182 | 367.2609 | 223.0435 | 3.4636 |  | 0 | 0.5 |  |  | 60.3182
No. of < Spec | 6 | -- | 0 | -- | -- | -- | -- | -- | -- | 22 | -- | -- | -- | -- | -- | --
No. of > Spec | 4 | 21 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 28.5714 | -- | 0 | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 19.0476 | 95.4545 | 0 |  | 0 | 0 |  | -- | 0 | 0 |  |  | 0 |  |  | 0