## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.05.23 | 7.8 | 20 | 0 | 1973 | 1293 | 593 | 348 | 245 | 233 | 6.9 | 118 | NIL | 0.4 | 20 | 874 | 122
02.05.23 | 7.6 | 22 | 0 | 1896 | 1270 | 588 | 340 | 248 | 229 | 6.7 | 113 | NIL | 0.3 | 22 | 893 | 123
03.05.23 | 7.8 | 23 | 0.2 | 1836 | 1230 | 580 | 332 | 204 | 244 | 6.9 | 112 | NIL | 0.4 | 23 | 754 | 130
04.05.23 | 7.7 | 14 | 0.2 | 1736 | 1160 | 600 | 354 | 246 | 204 | 5.9 | 100 | NIL | 0.4 | 14 | 901 | 120
05.05.23 | 7.6 | 15 | 0.2 | 1718 | 1150 | 615 | 362 | 253 | 206 | 6.5 | 109 | NIL | 0.4 | 15 | 901 | 122
06.05.23 | 7.6 | 14 | 0.2 | 1683 | 1128 | 623 | 371 | 252 | 213 | 6.4 | 110 | NIL | 0.4 | 14 | 883 | 116
07.05.23 | 7.6 | 14 | 0.2 | 1683 | 1128 | 623 | 371 | 252 | 213 | 6.4 | 110 | NIL | 0.4 | 14 | 890 | 116
08.05.23 | 7.8 | 20 | 0.1 | 1749 | 1172 | 633 | 382 | 251 | 216 | 6.1 | 114 | NIL | 0.4 | 20 | 893 | 120
09.05.23 | 7.6 | 18 | 0.1 | 1686 | 1130 | 628 | 379 | 249 | 230 | 6.3 | 114 | NIL | 0.4 | 18 | 754 | 115
10.05.23 | 8 | 20 | 0.1 | 1556 | 1093 | 596 | 420 | 176 | 250 | 6.4 | 115 | NIL | 0.4 | 20 | 885 | 123
11.05.23 | 8.1 | 22 | 0.1 | 1580 | 1074 | 574 | 400 | 174 | 244 | 6 | 113 | NIL | 0.4 | 22 | 881 | 120
12.05.23 | 7.9 | 32 | 0 | 1463 | 980 | 623 | 450 | 173 | 219 | 6 | 118 | NIL | 0.4 | 32 | 890 | 125
13.05.23 | 8 | 34 | 0 | 1436 | 962 | 610 | 436 | 174 | 216 | 6.3 | 114 | NIL | 0.4 | 34 | 894 | 129
14.05.24 | 8 | 34 | 0 | 1436 | 962 | 610 | 436 | 174 | 216 | 6.3 | 114 | NIL | 0.4 | 34 | 899 | 129
15.05.23 | 8.2 | 40 | 0 | 1478 | 990 | 512 | 302 | 210 | 305 | 6.5 | 120 | NIL | 0.2 | 40 | 878 | 100
16.05.23 | 8.1 | 23 | 0.5 | 1346 | 902 | 475 | 296 | 179 | 209 | 6 | 114 | NIL | 0.4 | 23 | 916 | 112
17.05.23 | 8 | 20 | 0.2 | 1452 | 973 | 467 | 288 | 179 | 216 | 6.2 | 116 | NIL | 0.4 | 20 | 929 | 102
18.05.23 | 7.9 | 22 | 0.3 | 1455 | 975 | 458 | 292 | 166 | 209 | 5.6 | 120 | NIL | 0.4 | 22 | 870 | 118
19.05.23 | 7.8 | 28 | 0.6 | 1463 | 980 | 484 | 301 | 183 | 230 | 6 | 118 | NIL | 0.4 | 28 | 879 | 122
20.05.23 | 7.7 | 32 | 0.4 | 1487 | 996 | 506 | 314 | 198 | 209 | 6.6 | 109 | NIL | 0.4 | 32 | 875 | 126
21.05.23 | 8.1 | 18 | 0.2 | 1448 | 970 | 480 | 301 | 179 | 216 | 5.9 | 122 | NIL | 0.4 | 18 | 888 | 113
22.05.23 | 7.7 | 33 | 0.6 | 1478 | 990 | 449 | 281 | 168 | 213 | 6 | 118 | NIL | 0.2 | 33 | 878 | 110
23.05.23 | 8.1 | 19 | 0.1 | 1473 | 987 | 514 | 323 | 191 | 230 | 6.6 | 119 | NIL | 0.4 | 19 | 881 | 118
24.05.23 | 8 | 16 | 0.3 | 1332 | 893 | 501 | 314 | 187 | 223 | 6.4 | 119 | NIL | 0.4 | 16 | 882 | 110
25.05.23 | 8.1 | 15 | 0.2 | 1313 | 880 | 523 | 349 | 174 | 216 | 6.5 | 120 | NIL | 0.4 | 15 | 892 | 114
26.05.23 | 7.9 | 14 | 0 | 1334 | 894 | 514 | 340 | 174 | 209 | 6.5 | 116 | NIL | 0.4 | 14 | 890 | 112
27.05.23 | 7.7 | 22 | 0.5 | 1388 | 930 | 506 | 331 | 175 | 202 | 7 | 114 | NIL | 0.4 | 22 | 887 | 120
28.05.23 | 7.7 | 22 | 0.5 | 1388 | 930 | 506 | 331 | 175 | 202 | 7 | 114 | NIL | 0.4 | 22 | 891 | 120
29.05.23 | 7.9 | 21 | 0 | 1328 | 890 | 480 | 301 | 179 | 209 | 6.5 | 115 | NIL | 0.4 | 21 | 910 | 118
30.05.23 | 7.8 | 22 | 0.5 | 1254 | 840 | 471 | 292 | 179 | 202 | 6 | 110 | NIL | 0.4 | 22 | 873 | 112
31.05.23 | 7.8 | 27 | 0.4 | 1274 | 854 | 483 | 310 | 173 | 210 | 6.5 | 114 | NIL | 0.4 | 27 | 875 | 119
MIN. | 7.6 | 17 | 0 | 1254 | 840 | 449 | 281 | 166 | 142 | 5.8 | 100 | 0 | 0.2 | 14 | 754 | 100
MAX. | 8.2 | 28 | 0.6 | 1973 | 1293 | 633 | 450 | 253 | 305 | 10.5 | 122 | 0 | 0.4 | 40 | 929 | 130
AVG. | 7.8581 | 19 | 0.21613 | 1520.0645 | 1019.5484 | 542.7419 | 343.4516 | 198.0645 | 218.2812 | 6.3516 | 114.5806 | 0 | 0.38333 | 22.4516 | 880.1935 | 117.9355
No. of < Spec | 0 | -- | 13 | -- | -- | -- | -- | -- | -- | 3 | -- | -- | -- | -- | -- | --
No. of > Spec | 6 | 17 | 2 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- | 41.9355 | -- | -- | -- | -- | -- | -- | 9.6774 | [5 empty] | --
% > Specs. | 19.3548 | 54.8387 | 6.4516 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0