## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2023-11-01 | 8.7 | 22 | NIL | 1840 | 1233 | 719 | 253 | 466 | 295 | 4.4 | - | NIL | 0.6 |  |  | 176
2023-11-02 | 7.98 | 28 | NIL | 1791 | 1200 | 701 | 240 | 461 | 273 | 4.7 | - | NIL | 0.6 |  |  | 169
2023-11-03 | 8.26 | 23 | NIL | 1655 | 1109 | 687 | 339 | 348 | 266 | 5.2 | - | NIL | 0.5 |  |  | 172
2023-11-04 | 8.73 | 25 | NIL | 1575 | 1055 | 704 | 334 | 370 | 275 | 4.8 | - | NIL | 0.5 |  |  | 167
2023-11-06 | 8.12 | 52 | NIL | 1716 | 1150 | 717 | 330 | 387 | 275 | 4.2 | - | NIL | 0.5 |  |  | 176
2023-11-07 | 8.67 | 35 | NIL | 1672 | 1120 | 730 | 352 | 378 | 260 | 4 | - | NIL | 0.5 |  |  | 168
2023-11-08 | 8.72 | 32 | NIL | 1628 | 1091 | 717 | 343 | 374 | 267 | 4.1 | - | NIL | 0.5 |  |  | 171
2023-11-09 | 8.54 | 25 | NIL | 1611 | 1080 | 726 | 334 | 392 | 282 | 4 | - | NIL | 0.5 |  |  | 166
2023-11-10 | 8.21 | 24 | NIL | 1488 | 997 | 717 | 334 | 383 | 246 | 3.9 | - | NIL | 0.5 |  |  | 156
2023-11-11 | 8.35 | 27 | NIL | 1490 | 998 | 673 | 334 | 339 | 231 | 3.2 | - | NIL | 0.5 |  |  | 163
2023-11-17 | 7.7 | 20 | NIL | 1292 | 866 | 717 | 348 | 369 | 224 | 4 | - | NIL | 0.5 |  |  | 42
2023-11-20 | 7.56 | 22 | NIL | 1418 | 950 | 781 | 334 | 447 | 253 | 3.5 | - | NIL | 0.5 |  |  | -
2023-11-20 | 7.65 | 13 | NIL | 1504 | 1008 | 845 | 444 | 401 | 246 | 3.3 | - | NIL | 0.5 |  |  | 134
2023-11-21 | 7.86 | 24 | NIL | 1291 | 865 | 752 | 326 | 426 | 246 | 3.3 | - | NIL | 0.5 |  |  | 3.4
2023-11-22 | 7.41 | 37 | NIL | 1254 | 840 | 757 | 317 | 440 | 239 | 2.9 | - | NIL | 0.5 |  |  | 3.1
2023-11-23 | 7.49 | 35 | NIL | 1291 | 865 | 770 | 321 | 449 | 239 | 3.2 | - | NIL | 0.5 |  |  | 29
2023-11-24 | 8.9 | 36 | NIL | 1365 | 915 | 796 | 334 | 462 | 253 | 3.6 | - | NIL | 0.5 |  |  | 360
2023-11-28 | 8.31 | 36 | NIL | 1416 | 949 | 814 | 365 | 449 | 253 | 3.1 | - | NIL | 0.5
2023-11-29 | 8.26 | 42 | NIL | 1470 | 985 | 805 | 370 | 435 | 275 | 3.3 | - | NIL | 0.5 |  |  | 77
2023-11-30 | 7.79 | 30 | NIL | 1388 | 930 | 796 | 356 | 440 | 253 | 3.2 | - | NIL | 0.5 |  |  | 65
[8 empty] | 0 |  |  |  | NIL
MIN. | 7.41 | 17 | 0 | 1254 | 840 | 673 | 240 | 0 | 142 | 5.8 | 0 | 0 | 0.5 | 0 | 0 | 3.1
MAX. | 8.9 | 28 | 0 | 1840 | 1233 | 845 | 444 | 466 | 295 | 10.5 | 0 | 0 | 0.6 | 0 | 0 | 360
AVG. | 8.1605 | 19 |  | 1507.75 | 1010.3 | 746.2 | 335.4 | 391.2381 | 252.0476 | 3.795 |  | 0 | 0.50526 |  |  | 133.1944
No. of < Spec | 2 | -- | 0 | -- | -- | -- | -- | -- | -- | 20 | -- | -- | -- | -- | -- | --
No. of > Spec | 12 | 18 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 1
% < Specs. | 10 | -- |  | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 60 | 90 |  |  | 0 | 0 |  | -- | 0 | 0 |  |  | 0 |  |  | 5.5556