## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.06.22 | 7.9 | 36 | 0 | 1866 | 1250 | 754 | 428 | 326 | 219 | 5.6 | 122 | NIL | 0.2 | 36 | 874 | 138
02.06.22 | 7.8 | 32 | 0 | 1937 | 1298 | 769 | 432 | 337 | 211 | 6.2 | 114 | NIL | 0.2 | 32 | 754 | 130
03.06.22 | 7.9 | 27 | 0 | 2149 | 1440 | 916 | 510 | 406 | 202 | 6.7 | 114 | NIL | 0.2 | 27 | 754 | 127
04.06.22 | 8.2 | 34 | 0 | 1640 | 1098 | 692 | 410 | 282 | 204 | 6 | 130 | NIL | 0.2 | 34 | 893 | 124
05.06.22 | 8.2 | 34 | 0 | 1640 | 1098 | 692 | 410 | 282 | 204 | 6 | 130 | NIL | 0.2 | 34 | 893 | 124
06.06.22 | 8.4 | 42 | 0 | 1660 | 1112 | 750 | 423 | 327 | 207 | 5.3 | 129 | NIL | 0.2 | 42 | 873 | 123
07.06.22 | 8.3 | 36 | 0 | 1693 | 1134 | 714 | 400 | 314 | 200 | 5.8 | 128 | NIL | 0.2 | 36 | 893 | 129
08.06.22 | 8 | 33 | 0 | 1537 | 1030 | 670 | 398 | 272 | 172 | 5.9 | 129 | NIL | 0.4 | 33 | 754 | 120
09.06.22 | 8.2 | 37 | 0 | 1507 | 1010 | 527 | 302 | 225 | 110 | 5.4 | 120 | NIL | 0.2 | 37 | 894 | 116
10.06.22 | 8.5 | 28 | 0 | 1358 | 910 | 533 | 306 | 227 | 105 | 5.8 | 133 | NIL | 0.3 | 28 | 894 | 137
11.06.22 | 8.1 | 28 | 0 | 1254 | 840 | 528 | 297 | 231 | 101 | 6.3 | 134 | NIL | 0.4 | 28 | 890 | 128
12.06.22 | 8.1 | 28 | 0 | 1254 | 840 | 528 | 297 | 231 | 101 | 6.3 | 134 | NIL | 0.4 | 28 | 890 | 128
13.06.22 | 8.3 | 40 | 0 | 1333 | 893 | 533 | 280 | 253 | 105 | 5.8 | 133 | NIL | 0.4 | 40 | 878 | 130
14.06.22 | 8.3 | 39 | 0 | 1318 | 880 | 520 | 272 | 248 | 108 | 6 | 130 | NIL | 0.4 | 39 | 916 | 134
15.06.22 | 8.5 | 35 | 0 | 1279 | 857 | 657 | 337 | 320 | 101 | 6.2 | 136 | NIL | 0.3 | 35 | 929 | 100
16.06.22 | 8.4 | 40 | 0 | 1448 | 970 | 675 | 382 | 293 | 93 | 6.1 | 132 | NIL | 0.3 | 40 | 929 | 118
17.06.22 | 7.5 | 28 | 0 | 1540 | 1032 | 684 | 395 | 289 | 110 | 6.4 | 128 | NIL | 0.3 | 28 | 929 | 127
18.06.22 | 7.9 | 27 | 0 | 1498 | 1020 | 674 | 382 | 292 | 112 | 6.3 | 130 | NIL | 0.3 | 27 | 875 | 134
19.06.22 | 7.9 | 27 | 0 | 1498 | 1020 | 674 | 382 | 292 | 112 | 6.3 | 130 | NIL | 0.3 | 27 | 875 | 134
20.06.22 | 8.2 | 24 | 0 | 1231 | 825 | 453 | 302 | 151 | 105 | 6.1 | 119 | NIL | 0.3 | 24 | 878 | 138
21.06.22 | 8.4 | 22 | 0 | 1119 | 750 | 441 | 295 | 146 | 101 | 6.7 | 139 | NIL | 0.2 | 22 | 881 | 123
22.06.22 | 8.5 | 20 | 0 | 1060 | 710 | 435 | 284 | 151 | 110 | 5.7 | 142 | NIL | 0.2 | 20 | 884 | 121
23.06.22 | 8.4 | 16 | 0 | 1030 | 690 | 395 | 253 | 142 | 84 | 5.9 | 145 | NIL | 0.2 | 16 | 884 | 100
24.06.22 | 7.4 | 19 | 0 | 1129 | 757 | 415 | 275 | 140 | 93 | 6.3 | 122 | NIL | 0.2 | 19 | 884 | 133
25.06.22 | 7.9 | 21 | 0 | 1146 | 768 | 422 | 289 | 133 | 101 | 5.7 | 118 | NIL | 0.4 | 21 | 890 | 122
26.06.22 | 7.9 | 21 | 0 | 1146 | 768 | 422 | 289 | 133 | 101 | 5.7 | 118 | NIL | 0.4 | 21 | 890 | 122
27.06.22 | 8.1 | 20 | 0 | 1168 | 776 | 440 | 296 | 144 | 105 | 5.9 | 122 | NIL | 0.4 | 20 | 899 | 120
28.06.22 | 8.3 | 27 | 0 | 1245 | 840 | 451 | 306 | 145 | 114 | 6.2 | 120 | NIL | 0.4 | 27 | 905 | 145
29.06.22 | 8.4 | 30 | 0 | 1469 | 984 | 457 | 320 | 137 | 122 | 6.7 | 136 | NIL | 0.4 | 30 | 881 | 149
30.06.22 | 8.2 | 26 | 0 | 1702 | 1144 | 617 | 346 | 271 | 156 | 6 | 133 | NIL | 0.4 | 26 | 890 | 153
MIN. | 7.4 | 17 | 0 | 1030 | 690 | 395 | 253 | 133 | 142 | 5.8 | 114 | 0 | 0.2 | 16 | 754 | 100
MAX. | 8.5 | 28 | 0 | 2149 | 1440 | 916 | 510 | 406 | 219 | 10.5 | 145 | 0 | 0.4 | 42 | 929 | 153
AVG. | 8.1367 | 19 | 0 | 1428.4667 | 958.1333 | 581.2667 | 343.2667 | 238 | 132.6129 | 6.0433 | 128.3333 | 0 | 0.3 | 29.2333 | 878.4333 | 127.5667
No. of < Spec | 1 | -- | 30 | -- | -- | -- | -- | -- | -- | 12 | -- | -- | -- | -- | -- | --
No. of > Spec | 20 | 26 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 3.3333 | -- | 100 | -- | -- | -- | -- | -- | -- | 40 | [5 empty] | --
% > Specs. | 66.6667 | 86.6667 | 0 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0