## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.05.23 | 8.1 | 15 | 0.2 | 2574 | 1740 | 910 | 540 | 370 | 334 | 6 | 120 | NIL | 0.5 | 15 | 910 | 150
02.05.23 | 7.9 | 13 | 0.1 | 2537 | 1700 | 907 | 519 | 388 | 328 | 6.3 | 119 | NIL | 0.5 | 13 | 864 | 149
03.05.23 | 7.9 | 15 | 0.1 | 2310 | 1548 | 894 | 506 | 388 | 312 | 6.7 | 116 | NIL | 0.5 | 15 | 754 | 152
04.05.23 | 7.9 | 14 | 0 | 2490 | 1596 | 874 | 509 | 365 | 240 | 6 | 118 | NIL | 0.5 | 14 | 864 | 140
05.05.23 | 7.8 | 13 | 0 | 2507 | 1680 | 898 | 519 | 379 | 244 | 6.3 | 120 | NIL | 0.5 | 13 | 860 | 142
06.05.23 | 7.8 | 13 | 0 | 2364 | 1584 | 885 | 510 | 375 | 236 | 6 | 114 | NIL | 0.5 | 13 | 873 | 139
07.05.23 | 8.3 | 19 | 0 | 2373 | 1590 | 870 | 502 | 368 | 230 | 6.9 | 118 | NIL | 0.5 | 19 | 910 | 135
08.05.23 | 8.3 | 19 | 0 | 2373 | 1590 | 870 | 502 | 368 | 230 | 6.9 | 118 | NIL | 0.5 | 19 | 910 | 135
09.05.23 | 8.1 | 22 | 0.5 | 2634 | 1765 | 885 | 506 | 379 | 240 | 6 | 119 | NIL | 0.5 | 22 | 864 | 145
10.05.23 | 8.2 | 38 | 0.6 | 2507 | 1680 | 872 | 489 | 383 | 229 | 6.2 | 122 | NIL | 0.5 | 38 | 887 | 135
11.05.23 | 8.2 | 35 | 0.5 | 2671 | 1790 | 850 | 475 | 375 | 218 | 6.8 | 120 | NIL | 0.5 | 35 | 875 | 130
12.05.23 | 7.8 | 62 | 0.7 | 2432 | 1630 | 864 | 489 | 375 | 250 | 7.2 | 100 | NIL | 0.5 | 62 | 888 | 148
13.05.23 | 7.8 | 68 | 0.9 | 2463 | 1650 | 859 | 475 | 384 | 259 | 6.9 | 104 | NIL | 0.4 | 68 | 877 | 152
14.05.23 | 7.8 | 68 | 0.9 | 2463 | 1650 | 859 | 475 | 384 | 259 | 6.9 | 104 | NIL | 0.4 | 68 | 872 | 152
15.05.23 | 8 | 46 | 0.1 | 2284 | 1530 | 501 | 305 | 196 | 223 | 6.8 | 100 | NIL | 0.6 | 46 | 869 | 100
16.05.23 | 7.9 | 32 | 0.6 | 2254 | 1510 | 855 | 480 | 375 | 257 | 6.9 | 100 | NIL | 0.5 | 32 | 958 | 140
17.05.23 | 7.8 | 28 | 0.4 | 2149 | 1440 | 837 | 471 | 366 | 237 | 6.5 | 112 | NIL | 0.6 | 28 | 878 | 134
18.05.23 | 7.5 | 34 | 0.5 | 2403 | 1610 | 850 | 480 | 370 | 250 | 6.7 | 100 | NIL | 0.6 | 34 | 871 | 130
19.05.23 | 7.5 | 36 | 0.9 | 2373 | 1590 | 868 | 493 | 375 | 244 | 6 | 110 | NIL | 0.6 | 36 | 873 | 148
20.05.23 | 7.9 | 34 | 0.4 | 2522 | 1690 | 876 | 510 | 366 | 230 | 6.2 | 114 | NIL | 0.6 | 34 | 864 | 142
21.05.23 | 7.4 | 47 | 0.2 | 2237 | 1500 | 881 | 501 | 380 | 237 | 6 | 100 | NIL | 0.5 | 47 | 878 | 139
22.05.23 | 7.4 | 47 | 0.2 | 2237 | 1500 | 881 | 501 | 380 | 237 | 6 | 100 | NIL | 0.5 | 47 | 881 | 139
23.05.23 | 8 | 55 | 0.1 | 2462 | 1650 | 894 | 519 | 375 | 230 | 6.6 | 110 | NIL | 0.5 | 55 | 984 | 145
24.05.23 | 7.8 | 40 | 0 | 2179 | 1460 | 885 | 510 | 375 | 226 | 6.9 | 114 | NIL | 0.5 | 40 | 982 | 140
25.05.23 | 7.9 | 39 | 0 | 2194 | 1470 | 920 | 523 | 397 | 244 | 7 | 118 | NIL | 0.5 | 39 | 875 | 137
26.05.23 | 7.5 | 26 | 0 | 2254 | 1510 | 907 | 514 | 393 | 237 | 6.8 | 110 | NIL | 0.5 | 26 | 960 | 147
27.05.23 | 8 | 26 | 0.2 | 2223 | 1490 | 911 | 532 | 379 | 316 | 7.2 | 120 | NIL | 0.5 | 26 | 893 | 156
28.05.23 | 8 | 26 | 0.2 | 2223 | 1490 | 911 | 532 | 379 | 316 | 7.2 | 120 | NIL | 0.5 | 26 | 888 | 156
29.05.23 | 7.5 | 22 | 0.6 | 2149 | 1440 | 894 | 506 | 388 | 230 | 6.9 | 112 | NIL | 0.5 | 22 | 872 | 140
30.05.23 | 7.7 | 30 | 0.6 | 2090 | 1400 | 881 | 492 | 389 | 223 | 6.4 | 100 | NIL | 0.5 | 30 | 893 | 137
31.05.23 | 7.6 | 33 | 0.5 | 2074 | 1390 | 873 | 480 | 393 | 220 | 6.2 | 112 | NIL | 0.5 | 33 | 890 | 132
MIN | 7.4 | 17 | 0 | 2074 | 1390 | 501 | 305 | 196 | 142 | 5.8 | 100 | 0 | 0.4 | 13 | 754 | 100
MAX. | 8.3 | 28 | 0.9 | 2671 | 1790 | 920 | 540 | 397 | 334 | 10.5 | 122 | 0 | 0.6 | 68 | 984 | 156
AVG. | 7.8484 | 19 | 0.32258 | 2355 | 1576.2258 | 868.4516 | 495.6452 | 372.8065 | 247.125 | 6.5613 | 111.7419 | 0 | 0.51 | 32.7419 | 887.6452 | 140.8387
No. of < Spec | 2 | -- | 12 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 6 | 23 | 8 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 6.4516 | -- | 38.7097 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | --
% > Specs. | 19.3548 | 74.1935 | 25.8065 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0