## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2024-02-01 | 7.05 | 27 | NIL | 2461 | 1649 | 823 | 443 | 380 | 274 | 4.1 | - | NIL | 0.5 |  |  | 70
2024-02-02 | 7.61 | 20 | NIL | 2483 | 1664 | 793 | 407 | 386 | 259 | 3.6 | - | NIL | 0.5 |  |  | 63
2024-02-03 | 7.5 | 13 | NIL | 2263 | 1516 | 814 | 420 | 394 | 252 | 3.2 | - | NIL | 0.5 |  |  | 62
2024-02-05 | 7.35 | 12 | NIL | 2382 | 1596 | 852 | 437 | 415 | 215 | 2.9 | - | NIL | 0.5 |  |  | 66
2024-02-06 | 7.1 | 37 | NIL | 2120 | 1421 | 810 | 424 | 386 | 237 | 3.1 | - | NIL | 0.5 |  |  | 69
2024-02-07 | 7.55 | 15 | NIL | 2261 | 1515 | 831 | 445 | 386 | 259 | 2.8 | - | NIL | 0.5 |  |  | 61
2024-02-08 | 7.77 | 39 | 0.5 | 2071 | 1388 | 750 | 428 | 322 | 252 | 2.5 | - | NIL | 0.5 |  |  | 69
2024-02-09 | 7.51 | 53 | 0.5 | 1968 | 1319 | 776 | 437 | 339 | 266 | 2.8 | - | NIL | 0.5 |  |  | 72
2024-02-10 | 7.29 | 39 | 0.5 | 2022 | 1355 | 767 | 420 | 347 | 244 | 3.1 | - | NIL | 0.5 |  |  | 66
2024-02-12 | 7.66 | 30 | NIL | 1673 | 1121 | 636 | 301 | 335 | 244 | 3.4 | - | NIL | 0.5 |  |  | 72
2024-02-13 | 7.19 | 28 | NIL | 1611 | 1080 | 644 | 310 | 334 | 259 | 3.1 | - | NIL | 0.5 |  |  | 68
2024-02-14 | 7.27 | 25 | NIL | 2094 | 1403 | 704 | 301 | 403 | 244 | 2.8 | - | NIL | 0.5 |  |  | 72
2024-02-15 | 7.55 | 21 | NIL | 2008 | 1346 | 691 | 288 | 403 | 229 | 3.2 | - | NIL | 0.5 |  |  | 71
2024-02-16 | 7.84 | 15 | NIL | 2034 | 1363 | 742 | 267 | 475 | 215 | 2.8 | - | NIL | 0.5 |  |  | 68
2024-02-20 | 7.29 | 14 | NIL | 2619 | 1755 | 784 | 479 | 305 | 244 | 3.1 | - | NIL | 0.5 |  |  | 56
2024-02-21 | 7.41 | 24 | NIL | 2612 | 1750 | 810 | 471 | 339 | 222 | 3.3 | - | NIL | 0.5 |  |  | 66
2024-02-22 | 7.5 | 24 | NIL | 2544 | 1705 | 797 | 458 | 339 | 237 | 3.1 | - | NIL | 0.5 |  |  | 61
2024-02-23 | 7.27 | 17 | NIL | 2878 | 1928 | 818 | 488 | 330 | 259 | 2.8 | - | NIL | 0.5 |  |  | 55
2024-02-26 | 7.76 | 48 | NIL | 2478 | 1660 | 907 | 522 | 385 | 281 | 3.9 | - | NIL | 0.5 |  |  | 68
2024-02-27 | 7.34 | 39 | NIL | 2508 | 1681 | 895 | 509 | 386 | 224 | 4.1 | - | NIL | 0.5 |  |  | 65
2024-02-28 | 7.4 | 25 | NIL | 2397 | 1606 | 903 | 517 | 386 | 259 | 3.9 | - | NIL | 0.5 |  |  | 63
2024-02-29 | 7.42 | 26 | NIL | 2335 | 1565 | 912 | 522 | 390 | 281 | 4.1 | - | NIL | 0.5 |  |  | 69
NIL
NIL
NIL
NIL
NIL
NIL
MIN | 7.05 | 17 | 0.5 | 1611 | 1080 | 636 | 267 | 305 | 142 | 5.8 | 0 | 0 | 0.5 | 0 | 0 | 55
MAX. | 7.84 | 28 | 0.5 | 2878 | 1928 | 912 | 522 | 475 | 281 | 10.5 | 0 | 0 | 0.5 | 0 | 0 | 72
AVG. | 7.4377 | 19 | 0.5 | 2264.6364 | 1517.5455 | 793.5909 | 422.4545 | 371.1364 | 243.3913 | 3.2591 |  | 0 | 0.5 |  |  | 66
No. of < Spec | 12 | -- | 0 | -- | -- | -- | -- | -- | -- | 22 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 15 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 54.5455 | -- | 0 | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 0 | 68.1818 | 0 |  | 0 | 0 |  | -- | 0 | 0 |  |  | 0 |  |  | 0