## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.03.23 | 8.3 | 82 | 0.5 | 3164 | 2120 | 1071 | 605 | 466 | 343 | 6 | 120 | NIL | 0.4 | 82 | 910 | 123
02.03.23 | 8.3 | 85 | 0.4 | 3179 | 2130 | 1080 | 620 | 460 | 350 | 6.1 | 122 | NIL | 0.4 | 85 | 864 | 138
03.03.23 | 8.1 | 87 | 0.4 | 3194 | 2140 | 1072 | 610 | 462 | 346 | 6.2 | 119 | NIL | 0.3 | 87 | 754 | 135
04.03.23 | 8.2 | 84 | 0.3 | 3015 | 2020 | 1033 | 594 | 439 | 340 | 5.9 | 122 | NIL | 0.3 | 84 | 864 | 132
05.03.23 | 8.2 | 84 | 0.3 | 3015 | 2020 | 1033 | 594 | 439 | 340 | 5.9 | 122 | NIL | 0.3 | 84 | 864 | 132
06.03.23 | 7.9 | 74 | 0.3 | 2407 | 1613 | 890 | 517 | 373 | 320 | 5.9 | 110 | NIL | 0.3 | 74 | 873 | 133
07.03.23 | 7.9 | 84 | 0.3 | 2552 | 1710 | 940 | 554 | 386 | 289 | 6 | 100 | NIL | 0.3 | 84 | 864 | 140
09.03.23 | 8.2 | 78 | 0.1 | 2704 | 1812 | 945 | 546 | 399 | 274 | 5.7 | 116 | NIL | 0.3 | 78 | 873 | 142
10.03.23 | 7.8 | 80 | 0.1 | 2472 | 1656 | 916 | 533 | 383 | 274 | 6 | 100 | NIL | 0.3 | 80 | 864 | 133
11.03.23 | 8 | 51 | 0.2 | 2164 | 1450 | 874 | 509 | 365 | 240 | 6 | 112 | NIL | 0.3 | 51 | 875 | 128
12.03.23 | 8 | 51 | 0.2 | 2164 | 1450 | 874 | 509 | 365 | 240 | 6 | 112 | NIL | 0.3 | 51 | 875 | 128
13.03.23 | 7.8 | 54 | 0.2 | 2191 | 1468 | 882 | 512 | 370 | 244 | 6.1 | 110 | NIL | 0.3 | 54 | 875 | 123
14.03.23 | 8.2 | 35 | 0.4 | 1388 | 930 | 521 | 311 | 210 | 297 | 6.1 | 118 | NIL | 0.2 | 35 | 877 | 110
15.03.23 | 7.6 | 50 | 0.1 | 2134 | 1430 | 861 | 496 | 263 | 251 | 6.3 | 100 | NIL | 0.3 | 50 | 881 | 128
16.03.23 | 7.9 | 42 | 0.1 | 2104 | 1410 | 843 | 509 | 334 | 248 | 6.5 | 112 | NIL | 0.3 | 42 | 869 | 134
17.03.23 | 7.6 | 40 | 0 | 2254 | 1510 | 836 | 491 | 345 | 236 | 6 | 114 | NIL | 0.3 | 40 | 958 | 130
18.03.23 | 7.8 | 28 | 0 | 2000 | 1240 | 790 | 483 | 307 | 229 | 6.7 | 100 | NIL | 0.2 | 28 | 878 | 126
19.03.23 | 7.8 | 28 | 0 | 2000 | 1240 | 790 | 483 | 307 | 229 | 6.7 | 100 | NIL | 0.2 | 28 | 878 | 126
20.03.23 | 7.9 | 29 | 0.2 | 2313 | 1550 | 798 | 487 | 311 | 236 | 6.1 | 118 | NIL | 0.3 | 29 | 873 | 130
21.03.23 | 7.8 | 38 | 0 | 2033 | 1360 | 754 | 463 | 291 | 212 | 6.3 | 118 | NIL | 0.2 | 38 | 864 | 122
22.03.23 | 7.9 | 36 | 0 | 2015 | 1350 | 735 | 454 | 281 | 190 | 6.2 | 120 | NIL | 0.2 | 36 | 878 | 120
23.03.23 | 7.9 | 40 | 0.2 | 2012 | 1348 | 727 | 449 | 278 | 198 | 6.5 | 112 | NIL | 0.2 | 40 | 890 | 129
24.03.23 | 7.9 | 43 | 0.3 | 1791 | 1200 | 672 | 441 | 231 | 190 | 6 | 100 | NIL | 0.3 | 43 | 984 | 118
25.03.23 | 8 | 46 | 0 | 1925 | 1290 | 685 | 458 | 227 | 198 | 6.9 | 112 | NIL | 0.3 | 46 | 982 | 125
26.03.23 | 8 | 46 | 0 | 1925 | 1290 | 685 | 458 | 227 | 198 | 6.9 | 112 | NIL | 0.3 | 46 | 982 | 125
27.03.23 | 8.2 | 39 | 0.5 | 1806 | 1210 | 680 | 420 | 260 | 206 | 6 | 119 | NIL | 0.2 | 39 | 960 | 130
28.03.23 | 7.7 | 90 | 0.7 | 2224 | 1490 | 811 | 479 | 332 | 221 | 7.4 | 114 | NIL | 0.4 | 90 | 893 | 136
29.03.23 | 7.6 | 90 | 0.6 | 2000 | 1340 | 806 | 470 | 336 | 213 | 7.4 | 112 | NIL | 0.4 | 90 | 890 | 140
30.03.23 | 7.9 | 88 | 0.6 | 2090 | 1400 | 798 | 462 | 336 | 206 | 7.1 | 104 | NIL | 0.4 | 88 | 872 | 138
31.03.23 | 7.6 | 17 | 0 | 1388 | 930 | 521 | 311 | 210 | 142 | 5.8 | 100 | 0 | 0.2 | 28 | 754 | 110
MAX. | 8.3 | 28 | 0.7 | 3194 | 2140 | 1080 | 620 | 466 | 350 | 10.5 | 122 | 0 | 0.4 | 90 | 984 | 142
AVG. | 7.9448 | 19 | 0.24138 | 2283.9655 | 1523.3448 | 841.4483 | 500.5862 | 337.3448 | 250 | 6.3069 | 112.069 | 0 | 0.28929 | 58.6897 | 888.4138 | 129.4483
No. of < Spec | 0 | -- | 11 | -- | -- | -- | -- | -- | -- | 4 | -- | -- | -- | -- | -- | --
No. of > Spec | 8 | 29 | 3 | -- | 3 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- | 37.931 | -- | -- | -- | -- | -- | -- | 13.7931 | [5 empty] | --
% > Specs. | 27.5862 | 100 | 10.3448 |  | 10.3448 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0