## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.03.24 | 7.12 | 51 | 0.8 | 2582 | 1730 | 941 | 572 | 369 | 238 | 3.8 | - | NIL | 0.6 |  |  | 59
02.03.24 | 7.66 | 40 | NIL | 2686 | 1800 | 984 | 530 | 454 | 209 | 3.1 | - | NIL | 0.7 |  |  | 55
04.03.24 | 7.7 | 19 | NIL | 2805 | 1880 | 958 | 530 | 428 | 252 | 3.3 | - | NIL | 0.6 |  |  | 51
05.03.24 | 7.76 | 30 | NIL | 2850 | 1910 | 984 | 543 | 441 | 238 | 3.5 | - | NIL | 0.6 |  |  | 55
06.03.24 | 7.51 | 41 | NIL | 2753 | 1845 | 971 | 522 | 449 | 223 | 2.9 | - | NIL | 0.6 |  |  | 49
2024-03-07 | 7.46 | 38 | NIL | 3090 | 2070 | 984 | 526 | 458 | 216 | 2.5 | - | NIL | 0.6 |  |  | 51
09.03.24 | 7.6 | 29 | NIL | 3448 | 2310 | 1128 | 585 | 543 | 259 | 3.2 | - | NIL | 0.5 |  |  | 53
11.03.24 | 7.12 | 25 | NIL | 4641 | 3110 | 1433 | 789 | 644 | 303 | 3.8 | - | NIL | 0.5 |  |  | 67
2024-03-12 | 7.9 | 28 | NIL | 3403 | 2280 | 1412 | 776 | 636 | 274 | 3.6 | - | NIL | 0.6 |  |  | 61
2024-03-13 | 7.02 | 68 | 0.7 | 3850 | 2580 | 1389 | 744 | 645 | 288 | 3.7 | - | NIL | 0.5 |  |  | 57
2024-03-14 | 7.36 | 74 | 0.4 | 3402 | 2280 | 1364 | 724 | 640 | 274 | 3.5 | - | NIL | 0.5 |  |  | 62
15.03.24 | 7.29 | 55 | NIL | 2866 | 1920 | 1314 | 724 | 590 | 245 | 3.2 | - | NIL | 0.5 |  |  | 64
2024-03-18 | 7.21 | 27 | NIL | 2701 | 1810 | 1190 | 619 | 571 | 259 | 3.1 | - | NIL | 0.5 |  |  | 61
2024-03-19 | 8 | 20 | NIL | 2611 | 1750 | 1135 | 606 | 529 | 223 | 3.9 | - | NIL | 0.4 |  |  | 63
20.03.24 | 7.28 | 42 | NIL | 2629 | 1762 | 1140 | 597 | 543 | 238 | 3.6 | - | NIL | 0.5 |  |  | 76
2024-03-21 | 7.1 | 53 | NIL | 2912 | 1951 | 1126 | 593 | 533 | 231 | 3.5 | - | NIL | 0.5 |  |  | 75
2024-03-22 | 7.32 | 44 | 0.2 | 2701 | 1810 | 1154 | 597 | 557 | 259 | 3.3 | - | NIL | 0.6 |  |  | 69
2024-03-23 | 7.52 | 21 | NIL | 2425 | 1625 | 1149 | 593 | 556 | 245 | 3.2 | - | NIL | 0.5 |  |  | 74
2024-03-26 | 7.94 | 19 | NIL | 2552 | 1710 | 1072 | 588 | 484 | 225 | 3.1 | - | NIL | 0.5 |  |  | 73
2024-03-27 | 7.2 | 94 | 0.9 | 2733 | 1831 | 1058 | 570 | 488 | 233 | 3.5 | - | NIL | 0.5 |  |  | 69
2024-03-28 | 7.27 | 86 | 0.7 | 2435 | 1632 | 1053 | 565 | 488 | 218 | 3.3 | - | NIL | 0.5 |  |  | 65
2024-03-29 | 7.67 | 90 | NIL | 2618 | 1754 | 1076 | 602 | 474 | 233 | 3.5 | - | NIL | 0.6 |  |  | 74
2024-03-30 | 7.3 | 73 | NIL | 2670 | 1789 | 1067 | 625 | 442 | 189 | 3.2 | - | NIL | 0.6 |  |  | 84
[8 empty] | 0 |  |  |  | NIL
[8 empty] | 0 |  |  |  | NIL
[8 empty] | 0 |  |  |  | NIL
[8 empty] | 0 |  |  |  | NIL
[8 empty] | 0 |  |  |  | NIL
NIL
| 7.02 | 17 | 0.2 | 2425 | 1625 | 941 | 522 | 0 | 142 | 5.8 | 0 | 0 | 0.4 | 0 | 0 | 49
MAX. | 8 | 28 | 0.9 | 4641 | 3110 | 1433 | 789 | 645 | 303 | 10.5 | 0 | 0 | 0.7 | 0 | 0 | 84
AVG. | 7.4483 | 19 | 0.61667 | 2928.8261 | 1962.5652 | 1134 | 613.913 | 427.2143 | 238.0833 | 3.3609 |  | 0 | 0.54091 |  |  | 63.7826
No. of < Spec | 13 | -- | 0 | -- | -- | -- | -- | -- | -- | 23 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 20 | 4 | -- | 5 | 5 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 56.5217 | -- | 0 | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 0 | 86.9565 | 66.6667 |  | 21.7391 | 21.7391 |  | -- | 0 | 0 |  |  | 0 |  |  | 0