## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2023-11-01 | 7.83 | 21 | - | 2093 | 1401 | 823 | 312 | 511 | 266 | 3.1 | - | NIL | 0.7 |  |  | 158
2023-11-02 | 7.84 | 61 | NIL | 2181 | 1558 | 809 | 303 | 506 | 280 | 3.3 | - | NIL | 0.6 |  |  | 162
03.11.23 | 7.67 | 21 | NIL | 2131 | 1428 | 777 | 402 | 375 | 287 | 3.5 | - | NIL | 0.5 |  |  | 158
2023-11-04 | 7.7 | 26 | NIL | 1962 | 1315 | 818 | 378 | 440 | 311 | 3.8 | - | NIL | 0.5 |  |  | 186
2023-11-06 | 7.76 | 35 | NIL | 2015 | 1350 | 840 | 383 | 457 | 282 | 3.5 | - | NIL | 0.5 |  |  | 181
2023-11-07 | 7.9 | 22 | NIL | 1963 | 1315 | 845 | 378 | 467 | 275 | 3.4 | - | NIL | 0.5 |  |  | 188
2023-11-08 | 7.26 | 33 | NIL | 2119 | 1420 | 849 | 365 | 484 | 260 | 3.3 | - | NIL | 0.5 |  |  | 175
2023-11-09 | 7.88 | 19 | NIL | 1954 | 1309 | 858 | 378 | 480 | 282 | 3.5 | - | NIL | 0.5 |  |  | 179
2023-11-10 | 7.5 | 46 | 0.7 | 1934 | 1296 | 836 | 453 | 383 | 289 | 3.3 | - | NIL | 0.5 |  |  | 162
11.11.23 | 7.4 | 69 | NIL | 2034 | 1363 | 836 | 453 | 383 | 246 | 3.5 | - | NIL | - |  |  | 152
2023-11-17 | 7.67 | 30 | NIL | 1410 | 945 | 827 | 427 | 400 | 253 | 3.5 | - | NIL | 0.5 |  |  | 144
2023-11-21 | 7.33 | 22 | NIL | 1381 | 925 | 827 | 440 | 387 | 253 | 3.1 | - | NIL | 0.5 |  |  | 141
2023-11-22 | 7.11 | 41 | NIL | 1204 | 790 | 818 | 444 | 374 | 239 | 2.9 | - | NIL | 0.5 |  |  | 139
2023-11-23 | 7.29 | 24 | NIL | 1037 | 695 | 858 | 449 | 409 | 246 | 3.2 | - | NIL | 0.5 |  |  | 246
2023-11-24 | 7.99 | 59 | NIL | 919 | 616 | 937 | 532 | 405 | 224 | 3.2 | - | NIL | 0.5 |  |  | 124
2023-11-28 | 7.58 | 86 | NIL | 1210 | 811 | 968 | 524 | 444 | 253 | 3.4 | - | NIL | 0.5 |  |  | 149
2023-11-29 | 7.75 | 115 | NIL | 1260 | 844 | 950 | 532 | 418 | 239 | 3.1 | - | NIL | 0.5 |  |  | 141
2023-11-30 | 7.45 | 70 | NIL | 2054 | 1376 | 968 | 541 | 427 | 231 | 3.3 | - | NIL | 0.5 |  |  | 145
NIL
NIL
NIL
NIL
NIL
NIL
NIL
NIL
NIL
NIL
MIN | 7.11 | 17 | 0.7 | 919 | 616 | 777 | 303 | 374 | 142 | 5.8 | 0 | 0 | 0.5 | 0 | 0 | 124
MAX. | 7.99 | 28 | 0.7 | 2181 | 1558 | 968 | 541 | 511 | 311 | 10.5 | 0 | 0 | 0.6 | 0 | 0 | 246
AVG. | 7.6061 | 19 | 0.7 | 1714.5 | 1153.1667 | 858 | 427.4444 | 430.5556 | 255.6842 | 3.3278 |  | 0 | 0.50625 |  |  | 162.7778
No. of < Spec | 6 | -- | 0 | -- | -- | -- | -- | -- | -- | 18 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 17 | 1 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 4
% < Specs. | 33.3333 | -- | 0 | -- | -- | -- | -- | -- | -- | 100 | [5 empty] | --
% > Specs. | 0 | 94.4444 | 100 |  | 0 | 0 |  | -- | 0 | 0 |  |  | 0 |  |  | 22.2222