## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.09.23 | 7.35 | 33 | 0.4 | 2104 | 1410 | 735 | 386 | 349 | 355 | 6.9 | - | NIL | 0.7 |  |  | 166
2023-09-02 | 7.72 | 56 | 0.4 | 2037 | 1365 | 748 | 399 | 349 | 369 | 7.1 | 102 | NIL | 0.7 |  |  | 172
2023-09-04 | 7.56 | 21 | 0.3 | 1731 | 1160 | 617 | 314 | 303 | 282 | 5.9 | 110 | NIL | 0.5 |  |  | 121
2023-09-05 | 7.72 | 42 | NIL | 2701 | 1810 | 760 | 399 | 361 | 398 | 7.3 | - | NIL | 0.7 |  |  | 188
2023-09-06 | 7.36 | 32 | NIL | 2173 | 1456 | 718 | 365 | 353 | 291 | 7.1 | - | NIL | 0.7 |  |  | 181
2023-09-07 | 7.8 | 25 | NIL | 2294 | 1540 | 760 | 372 | 388 | 390 | 6.4 | - | NIL | 0.6 |  |  | 180
2023-09-08 | 7.73 | 26 | NIL | 2268 | 1520 | 714 | 357 | 357 | 398 | 6.5 | - | NIL | 0.7 |  |  | 184
2023-09-09 | 7.69 | 22 | NIL | 2074 | 1390 | 733 | 369 | 364 | 391 | 6.2 | - | NIL | 0.7 |  |  | 188
2023-09-11 | 6.92 | 16 | NIL | 2240 | 1501 | 757 | 365 | 392 | 391 | 6.4 | - | NIL | 0.6 |  |  | 179
2023-09-12 | 7.45 | 20 | NIL | 2209 | 1480 | 768 | 372 | 396 | 398 | 6 | - | NIL | 0.6 |  |  | 189
2023-09-13 | 7.41 | 17 | NIL | 2365 | 1585 | 760 | 376 | 384 | 405 | 6.2 | - | NIL | 0.7 |  |  | 182
2023-09-14 | 7.81 | 21 | 0.2 | 2011 | 1348 | 768 | 365 | 403 | 383 | 6.1 | - | NIL | 0.6 |  |  | 174
2023-09-15 | 7.72 | 24 | 0.3 | 2150 | 1427 | 776 | 396 | 380 | 376 | 6 | - | NIL | 0.6 |  |  | 179
2023-09-16 | 7.13 | 20 | 0.6 | 1940 | 1300 | 768 | 380 | 388 | 391 | 5.8 | - | NIL | 0.7 |  |  | 193
2023-09-18 | 7.56 | 20 | 0.3 | 1985 | 1330 | 811 | 384 | 427 | 362 | 5.1 | - | NIL | 0.7 |  |  | 193
2023-09-19 | 7.64 | 22 | 0.2 | 2020 | 1350 | 820 | 390 | 430 | 354 | 5.3 | - | NIL | 0.7 |  |  | 187
2023-09-20 | 7.24 | 30 | 0.7 | 1703 | 1141 | 795 | 392 | 403 | 369 | 5.3 | - | NIL | 0.7 |  |  | 189
2023-09-21 | 7.25 | 41 | 0.6 | 1752 | 1174 | 803 | 376 | 427 | 376 | 5.6 |  | NIL | 0.6 |  |  | 178
2023-09-22 | 7.28 | 42 | 0.7 | 1731 | 1160 | 799 | 380 | 419 | 369 | 5.2 | - | NIL | 0.6 |  |  | 182
2023-09-23 | 7.4 | 41 | NIL | 1789 | 1199 | 795 | 388 | 407 | 362 | 5.4 | - | NIL | 0.6 |  |  | 188
2023-09-25 | 7.56 | 38 | NIL | 1686 | 1130 | 757 | 369 | 388 | 311 | 5 | - | NIL | 0.6 |  |  | 163
2023-09-26 | 7.44 | 42 | 0.4 | 1564 | 1048 | 764 | 376 | 388 | 347 | 5.1 | - | NIL | 0.6 |  |  | 178
2023-09-27 | 7.74 | 45 | 0.7 | 1583 | 1061 | 784 | 384 | 400 | 369 | 5.3 | - | NIL | 0.6 |  |  | 186
2023-09-29 | 7.12 | 61 | 0.8 | 1957 | 1311 | 792 | 392 | 400 | 376 | 5.2 | - | NIL | 0.7 |  |  | 172
2023-09-30 | 7.21 | 59 | 0.6 | 2064 | 1383 | 795 | 380 | 415 | 362 | 5.1 | - | NIL | 0.6 |  |  | 178
NIL
NIL
NIL
MIN | 6.92 | 17 | 0.2 | 1564 | 1048 | 617 | 314 | 303 | 142 | 5.8 | 102 | 0 | 0.5 | 0 | 0 | 121
MAX. | 7.81 | 28 | 0.8 | 2701 | 1810 | 820 | 399 | 430 | 405 | 10.5 | 110 | 0 | 0.7 | 0 | 0 | 193
AVG. | 7.4724 | 19 | 0.48 | 2005.24 | 1343.16 | 763.88 | 377.04 | 386.84 | 358.3462 | 5.9 | 106 | 0 | 0.64167 |  |  | 178.8
No. of < Spec | 13 | -- | 0 | -- | -- | -- | -- | -- | -- | 13 | -- | -- | -- | -- | -- | --
No. of > Spec | 0 | 20 | 7 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 13
% < Specs. | 52 | -- | 0 | -- | -- | -- | -- | -- | -- | 52 | [5 empty] | --
% > Specs. | 0 | 80 | 46.6667 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  |  | 52