## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.01.22 | 7.6 | 29 | 0 | 3088 | 2069 | 821 | 484 | 337 | 331 | 6.6 | 118 | NIL | 0.2 | 29 | 910 | 160
02.01.22 | 7.5 | 84 | 0 | 3048 | 2033 | 996 | 884 | 112 | 412 | 6.5 | 116 | NIL | 0.2 | 84 | 864 | 158
03.01.22 | 7.7 | 26 | 0 | 2752 | 1844 | 839 | 496 | 343 | 329 | 6.9 | 112 | NIL | 0.2 | 26 | 754 | 163
04.01.22 | 7.7 | 27 | 0 | 3119 | 2090 | 886 | 570 | 316 | 342 | 6.9 | 120 | NIL | 0.2 | 27 | 864 | 170
05.01.22 | 8.1 | 27 | 0 | 3358 | 2250 | 1045 | 626 | 419 | 410 | 7.1 | 122 | NIL | 0.2 | 27 | 887 | 174
06.01.22 | 8.1 | 28 | 0 | 3149 | 2110 | 991 | 601 | 390 | 378 | 7 | 121 | NIL | 0.2 | 28 | 873 | 173
07.01.22 | 8 | 25 | 0 | 2970 | 1990 | 895 | 512 | 383 | 330 | 6.5 | 110 | NIL | 0.2 | 25 | 864 | 159
08.01.22 | 8 | 27 | 0 | 3363 | 2253 | 924 | 504 | 420 | 648 | 6.3 | 112 | NIL | 0.2 | 27 | 864 | 170
09.01.22 | 7.6 | 50 | 0 | 3746 | 2510 | 1084 | 692 | 392 | 570 | 6.8 | 112 | NIL | 0.3 | 50 | 887 | 220
10.01.22 | 7.8 | 32 | 0 | 4836 | 3240 | 1004 | 588 | 25 | 1094 | 7.2 | 120 | NIL | 0.2 | 32 | 873 | 189
11.01.22 | 7.2 | 33 | 0 | 4761 | 3190 | 1021 | 546 | 475 | 900 | 7 | 100 | NIL | 0.2 | 33 | 864 | 180
12.01.22 | 7.9 | 27 | 0 | 3851 | 2580 | 966 | 559 | 407 | 994 | 6.8 | 100 | NIL | 0.2 | 27 | 878 | 176
13.01.22 | 7.8 | 20 | 0 | 3567 | 2390 | 991 | 542 | 25 | 1022 | 7.1 | 119 |  | 0.2 | 20 | 890 | 184
15.01.22 | 7.7 | 22 | 0 | 3442 | 2240 | 982 | 536 | 446 | 959 | 7 | 112 |  | 0.2 | 22 | 877 | 180
16.01.22 | 7.6 | 32 | 0 | 2403 | 1610 | 806 | 567 | 239 | 502 | 6.9 | 114 | NIL | 0.2 | 32 | 881 | 186
17.01.22 | 7.7 | 27 | 0 | 3047 | 2024 | 785 | 462 | 323 | 770 | 7 | 100 | NIL | 0.2 | 27 | 869 | 162
20.01.22 | 8 | 40 | 0 | 2805 | 1880 | 861 | 528 | 333 | 664 | 6.4 | 120 | NIL | 0.2 | 40 | 878 | 173
21.01.22 | 8.1 | 38 | 0 | 2880 | 1930 | 903 | 550 | 353 | 744 | 6.4 | 112 | NIL | 0.2 | 38 | 893 | 160
22.01.22 | 8.4 | 32 | 0 | 3029 | 2030 | 924 | 512 | 412 | 730 | 6.9 | 100 | NIL | 0.2 | 32 | 873 | 174
23.01.22 | 8.1 | 33 | 0 | 2493 | 1670 | 818 | 572 | 246 | 428 | 5.8 | 110 | NIL | 0.2 | 33 | 864 | 163
24.01.22 | 8 | 34 | 0 | 2825 | 1893 | 932 | 564 | 368 | 766 | 6.1 | 120 | NIL | 0.2 | 34 | 878 | 175
25.01.22 | 7.9 | 42 | 0 | 2716 | 1820 | 916 | 594 | 322 | 752 | 6 | 116 | NIL | 0.2 | 42 | 890 | 169
27.01.22 | 8.3 | 47 | 0 | 2772 | 1850 | 926 | 538 | 27 | 762 | 6.4 | 124 | NIL | 0.2 | 47 | 893 | 186
28.01.22 | 8.1 | 38 | 0 | 2764 | 1839 | 907 | 529 |  | 732 | 6.2 | 110 | NIL | 0.2 | 38 | 878 | 182
29.01.22 | 8.4 | 52 | 0 | 3045 | 2040 | 806 | 504 | 2 | 591 | 6.2 | 124 | NIL | 0.2 | 52 | 893 | 167
30.01.22 | 7.6 | 26 | 0 | 2961 | 1984 | 825 | 564 |  | 320 | 6.4 | 110 | NIL | 0.2 | 26 | 873 | 150
31.01.22 | 7.9 | 34 | 0 | 2710 | 1820 | 890 | 520 |  | 720 | 6.7 | 102 | NIL | 0.2 | 34 | 864 | 170
.
MIN. | 7.2 | 17 | 0 | 2403 | 1610 | 785 | 462 | 2 | 142 | 5.8 | 100 | 0 | 0.2 | 20 | 754 | 150
MAX. | 8.4 | 28 | 0 | 4836 | 3240 | 1084 | 884 | 475 | 1094 | 10.5 | 124 | 0 | 0.3 | 84 | 910 | 220
AVG. | 7.8815 | 19 | 0 | 3166.6667 | 2117.7407 | 916.4444 | 560.8889 | 296.4583 | 619.3571 | 6.6333 | 113.1852 | 0 | 0.20385 | 34.5185 | 873.1852 | 173.0741
No. of < Spec | 1 | -- | 27 | -- | -- | -- | -- | -- | -- | 1 | -- | -- | -- | -- | -- | --
No. of > Spec | 8 | 26 | 0 | -- | 9 | 0 | -- | -- | 18 | 0 | 0 | -- | 0 | -- | 0 | 6
% < Specs. | 3.7037 | -- | 100 | -- | -- | -- | -- | -- | -- | 3.7037 | [5 empty] | --
% > Specs. | 29.6296 | 96.2963 | 0 |  | 33.3333 | 0 |  | -- | 66.6667 | 0 | 0 |  | 0 |  | 0 | 22.2222