## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | TSS | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | Max.20 PPM | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2024-09-02 | 8.85 | - |  | NIL |  | 875 | 425 | 262 | 163 | 130 | 7 | 295 | 6 | - |  |  | -
2024-09-03 | 8.8 | - |  | NIL | 1313 | 880 | 423 | 260 | 163 | 127 | 6.9 | 297 | 6 | - |  |  | -
2024-09-04 | 8.65 | - |  | NIL | 1291 | 865 | 427 | 263 | 164 | 130 | 6.7 | 302 | 6 | - |  |  | -
2024-09-05 | 8.98 | - |  | NIL | 1194 | 800 | 438 | 274 | 164 | 139 | 6.8 | 318 | 7 | - |  |  | -
2024-09-06 | 9.22 | - |  | NIL | 1102 | 720 | 350 | 224 | 126 | 142 | 7 | 300 | 8 | - |  |  | -
2024-09-07 | 9.28 | - |  | NIL | 1044 | 700 | 348 | 219 | 129 | 144 | 7.2 | 310 | 9 | - |  |  | -
2024-09-09 | 9.25 | 27 |  | NIL | 1077 | 722 | 353 | 229 | 124 | 146 | 6.9 | 315 | 8 | - |  |  | -
2024-09-10 | 8.84 | 20 |  | NIL | 1041 | 698 | 368 | 238 | 130 | 133 | 6.5 | 302 | 7 | - |  |  | -
11.09.24 | 8.9 | - |  | NIL | 1020 | 684 | 364 | 233 | 131 | 130 | 6.2 | 298 | 8 | - |  |  | -
2024-09-12 | 8.96 | 21 |  | NIL | 970 | 650 | 356 | 224 | 132 | 134 | 6 | 300 | 9 | - |  |  | -
2024-09-13 | 8.92 | - |  | NIL | 1004 | 673 | 360 | 229 | 131 | 140 | 6.2 | 303 | 9 | - |  |  | -
2024-09-14 | 8.87 | - |  | NIL | 1014 | 680 | 365 | 232 | 133 | 145 | 6.4 | 310 | 9 | - |  |  | -
2024-09-16 | 8.85 | 13 |  | NIL | 1132 | 759 | 344 | 213 | 131 | 122 | 6 | 290 | 4 | - |  |  | -
17.09.24 | 8.9 | 11 |  | NIL | 1140 | 764 | 369 | 233 | 136 | 128 | 6.2 | 302 | 5 | - |  |  | -
2024-09-18 | 9 | 12 |  | NIL | 1094 | 733 | 359 | 230 | 129 | 130 | 6.4 | 310 | 6 | - |  |  | -
2024-09-19 | 8.89 | 13 |  | NIL | 1073 | 724 | 346 | 213 | 133 | 124 | 6.6 | 308 | 5 | - |  |  | -
2024-09-20 | 8.86 | - |  | NIL | 1064 | 713 | 366 | 208 | 158 | 142 | 6 | 316 | 7 | - |  |  | -
2024-09-21 | 8.87 | 12 |  | NIL | 1053 | 703 | 354 | 200 | 154 | 140 | 6.4 | 310 | 6 | - |  |  | -
2024-09-23 | 8.78 | 14 |  | NIL | 1040 | 697 | 358 | 208 | 150 | 137 | 6.5 | 317 | 5 | - |  |  | -
2024-09-24 | 8.7 | 11 |  | NIL | 1014 | 680 | 369 | 212 | 157 | 129 | 6.4 | 320 | 4 | - |  |  | -
2024-09-25 | 8.78 | 12 |  | NIL | 1033 | 692 | 357 | 200 | 157 | 132 | 6 | 309 | 6 | - |  |  | -
2024-09-26 | 9.1 | 14 |  | NIL | 1030 | 690 | 398 | 264 | 134 | 140 | 6.5 | 320 | 9 | - |  |  | -
2024-09-27 | 9.09 | 18 |  | NIL | 1041 | 698 | 409 | 254 | 155 | 122 | 6.8 | 328 | 8 | - |  |  | -
2024-09-28 | 8.2 | 16 |  | NIL | 1164 | 780 | 456 | 293 | 163 | 120 | 7 | 340 | 10 | - |  |  | -
30.09.24 | 9.25 | 16 |  | NIL | 1149 | 770 | 444 | 290 | 154 | 127 | 6.9 | 332 | 9 | - |  |  | -
01.10.24 | 8.85 | 9.1 |  | NIL | 1179 | 790 | 475 | 296 | 179 | 122 | 7 | 325 | 9 | - |  |  | -
2024-10-02 | 9.18 | 15 |  | NIL | 1164 | 780 | 488 | 293 | 195 | 130 | 6.4 | 348 | 9 | - |  |  | -
03.10.24 | 8.93 | 15 |  | NIL | 1088 | 729 | 533 | 330 | 203 | 138 | 7 | 314 | 8 | - |  |  | -
2024-10-04 | 8.9 | 15 |  | NIL | 1097 | 735 | 545 | 337 | 208 | 132 | 7 | 310 | 8 | - |  |  | -
2024-10-05 | 8.93 | 15 |  | NIL | 1089 | 730 | 542 | 336 | 206 | 137 | 6.9 | 317 | 8 | - |  |  | -
2024-10-07 | 8.9 | - |  | NIL | 1124 | 753 | 473 |  | 473 | 120 | 7.1 | 339 | 6 | - |  |  | -
08.10.24 | 8.94 | - |  | NIL | 1119 | 750 | 470 | 291 | 179 | 126 | 6.8 | 344 | 7 | - |  |  | -
2024-10-09 | 9.25 | 10 |  | NIL | 1184 | 793 | 502 | 309 | 193 | 125 | 6.4 | 378 | 9 | - |  |  | -
10.10.24 | 9.3 | 13 |  | NIL | 1176 | 788 | 509 | 310 | 199 | 121 | 6.6 | 384 | 9 | - |  |  | -
11.10.24 | 9.09 | 15 |  | NIL | 1208 | 810 | 513 |  | 513 | 124 | 6.9 | 390 | 7 | - |  |  | -
2024-10-12 | 9.15 | 19 |  | NIL | 1219 | 817 | 507 | 314 | 193 | 130 | 6.7 | 390 | 7 | - |  |  | -
2024-10-14 | 8.8 | 18 |  | NIL | 1269 | 850 | 540 | 335 | 205 | 128 | 7 | 309 | 6 | - |  |  | -
15.10.24 | 9.25 | 16 |  | NIL | 1234 | 827 | 523 | 324 | 199 | 135 | 6.8 | 315 | 7 | - |  |  | -
16.10.24 | 9.2 | 7 |  | NIL | 1104 | 740 | 430 | 266 | 164 | 135 | 6.4 | 310 | 8 | - |  |  | -
17.10.24 | 9.4 | 13 |  | NIL | 1014 | 680 | 380 | 235 | 145 | 170 | 6.8 | 344 | 10 | - |  |  | -
18.10.24 | 9.3 | 12 |  | NIL | 1009 | 672 | 354 | 226 | 128 | 168 | 6 | 340 | 9 | - |  |  | -
19.10.24 | 9.27 | 12 |  | NIL | 1007 | 675 | 360 | 227 | 133 | 175 | 6.2 | 332 | 8 | - |  |  | -
21.10.24 | 9.2 | 13 |  | NIL | 1074 | 720 | 400 | 248 | 152 | 159 | 6.4 | 302 | 8 | - |  |  | -
22.10.24 | 9.1 | 12 |  | NIL | 1201 | 805 | 422 | 259 | 163 | 162 | 6.9 | 300 | 6 | - |  |  | -
23.10.24 | 9.15 | 12 |  | NIL | 1211 | 812 | 413 | 256 | 157 | 168 | 6.7 | 295 | 7 | - |  |  | -
24.10.24 | 9.2 | 10 |  | 1 | 1238 | 830 | 420 | 273 | 147 | 170 | 6.5 | 300 | 9 | - |  |  | -
25.10.24 | 9.14 | 11 |  | NIL | 1185 | 794 | 412 | 268 | 144 | 164 | 7 | 302 | 8 | - |  |  | -
2024-10-26 | 9.25 | 16 |  | 0.8 | 1200 | 804 | 423 | 274 | 149 | 159 | 6.4 | 318 | 9 | - |  |  | -
28.10.24 | 9.04 | 17 |  | NIL | 1108 | 743 | 403 | 264 | 139 | 142 | 6 | 300 | 6 | - |  |  | -
29.10.24 | 9.1 | 19 |  | 0.8 | 1100 | 737 | 410 | 264 | 146 | 148 | 6 | 307 | 7 | - |  |  | -
30.10.24 | 9.1 | 16 |  | 0.2 | 1119 | 750 | 395 | 254 | 141 | 140 | 6.8 | 298 | 6 | - |  |  | -
31.10.24 | 9.1 | 15 |  | 0.5 | 1030 | 690 | 410 | 269 | 141 | 140 | 6.8 | 304 | 8 | - |  |  | -
04.11.24 | 9 | 15 |  | 0.2 | 960 | 643 | 415 | 273 | 142 | 144 | 6 | 318 | 7 | - |  |  | -
05.11.24 | 9.1 | 14 |  | NIL | 925 | 620 | 422 | 280 | 142 | 140 | 6.3 | 321 | 9 | - |  |  | -
06.11.24 | 9.1 | 14 |  | NIL | 935 | 627 | 433 | 282 | 151 | 152 | 6.5 | 314 | 8 | - |  |  | -
07.11.24 | 9.08 | 11 |  | NIL | 955 | 640 | 440 | 284 | 156 | 160 | 6.5 | 320 | 9 | - |  |  | -
08.11.24 | 9.1 | 10 |  | 0.2 | 925 | 620 | 398 | 246 | 152 | 130 | 6.7 | 340 | 10 | - |  |  | -
09.11.24 | 9.02 | 11 |  | 0.3 | 886 | 594 | 350 | 233 | 117 | 120 | 6.9 | 310 | 8 | - |  |  | -
11.11.24 | 9.02 | 12 |  | 0.9 | 873 | 580 | 343 | 224 | 119 | 129 | 7.2 | 300 | 7 | - |  |  | -
12.11.24 | 9.14 | 14 |  | 0.2 | 885 | 593 | 350 | 239 | 111 | 132 | 7.4 | 308 | 9 | - |  |  | -
13.11.24 | 9.1 | 12 |  | 0.2 | 910 | 610 | 357 | 221 | 136 | 137 | 7.4 | 316 | 9 | - |  |  | -
14.11.24 | 9.28 | 13 |  | 0.4 | 943 | 632 | 330 | 214 | 116 | 133 | 6.9 | 310 | 8 | - |  |  | -
15.11.24 | 9.3 | 13 |  | 0.3 | 958 | 642 | 337 | 208 | 129 | 137 | 6.9 | 317 | 9 | - |  |  | -
16.11.24 | 9.26 | 15 |  | NIL | 973 | 652 | 345 | 213 | 132 | 142 | 7 | 324 | 9 | - |  |  | -
18.11.24 | 8.01 | 15 |  | 0.3 | 1014 | 680 | 357 | 221 | 136 | 155 | 6 | 130 | NIL | - |  |  | -
19.11.24 | 6.5 | 15 |  | NIL | 885 | 593 | 240 | 148 | 92 | 142 | 6.5 | 100 | NIL | - |  |  | -
20.11.24 | 7 |  |  | 0.5 | 939 | 629 | 250 | 155 | 95 | 139 | 7 | 92 | NIL | - |  |  | -
21.11.24 | 7.5 |  |  | NIL | 804 | 539 | 210 | 130 | 80 | 106 | 6.8 | 83 | NIL | - |  |  | -
22.11.24 | 7.6 | - |  | 0.2 | 776 | 520 | 200 | 124 | 76 | 94 | 7 | 74 | NIL | - |  |  | -
23.11.24 | 7.5 | - |  | 0.2 | 801 | 537 | 220 | 136 | 84 | 115 | 7.2 | 80 | NIL | - |  |  | -
25.11.24 | 8.1 | - |  | NIL | 887 | 594 | 240 | 150 | 90 | 118 | 6.9 | 86 | NIL | - |  |  | -
26.11.24 | 8.15 | - |  | 0.3 | 955 | 640 | 248 | 159 | 89 | 122 | 6.5 | 88 | NIL | - |  |  | -
27.11.24 | 7.65 | - |  | 0.3 | 925 | 620 | 200 | 126 | 74 | 95 | 6.5 | 100 | NIL | - |  |  | -
28.11.24 | 8.1 | - |  | 0.3 | 858 | 575 | 215 | 133 | 82 | 90 | 6.5 | 110 | NIL | - |  |  | -
29.11.24 | 8 | - |  | 0.2 | 880 | 590 | 212 | 131 | 81 | 124 | 6.3 | 100 | NIL | - |  |  | -
30.11.24 | 8 | - |  | 0.2 | 850 | 570 | 200 | 124 | 76 | 118 | 6.5 | 115 | NIL | - |  |  | -
02.12.24 | 8 | - |  | 0.2 | 805 | 540 | 192 | 119 | 73 | 107 | 6.7 | 150 | NIL | - |  |  | -
03.12.24 | 7.8 | - |  | 0.1 | 641 | 430 | 160 | 99 | 61 | 94 | 6.8 | 100 | NIL | - |  |  | -
04.12.24 | 8.4 | - |  | 0.2 | 613 | 411 | 200 | 125 | 75 | 96 | 7 | 100 | 2 | - |  |  | -
05.12.24 | 7.6 | - |  | 0.2 | 589 | 395 | 196 | 121 | 75 | 94 | 6.9 | 90 | NIL | - |  |  | -
06.12.24 | 6.5 | - |  | NIL | 650 | 436 | 210 | 130 | 80 | 100 | 7 | 98 | NIL | - |  |  | -
07.12.24 | 6.5 | - |  | NIL | 687 | 460 | 220 | 136 | 84 | 93 | 7.3 | 59 | NIL | - |  |  | -
09.12.24 | 6 | - |  | 0.2 | 634 | 425 | 200 | 124 | 76 | 106 | 7 | 50 | NIL | - |  |  | -
10.12.24 | 6.7 | - |  | 0.2 | 653 | 438 | 218 | 135 | 83 | 110 | 7.5 | 62 | NIL | - |  |  | -
11.12.24 | 7 | 32 |  | 0.2 | 650 | 436 | 226 | 140 | 86 | 117 | 7.3 | 69 | NIL | - |  |  | -
12.12.24 | 7.5 | - |  | 0.4 | 630 | 422 | 180 | 112 | 68 | 94 | 5.9 | 94 | NIL | - |  |  | -
13.12.24 | 7.9 | - |  | 0.2 | 671 | 450 | 192 | 119 | 73 | 99 | 6.2 | 93 | NIL | - |  |  | -
14.12.24 | 8.1 | - |  | NIL | 776 | 520 | 230 | 142 | 88 | 118 | 6.2 | 100 | NIL | - |  |  | -
16.12.24 | 8.2 | - |  | NIL | 850 | 570 | 215 | 133 | 82 | 112 | 6.5 | 110 | NIL | - |  |  | -
17.12.24 | 8 | - |  | NIL | 731 | 490 | 180 | 111 | 69 | 95 | 6.8 | 92 | NIL | - |  |  | -
18.12.24 | 8.1 | - |  | NIL | 643 | 431 | 195 | 120 | 75 | 107 | 6.6 | 100 | NIL | - |  |  | -
19.12.24 | 8.3 | - |  | NIL | 653 | 438 | 210 | 130 | 80 | 95 | 6.8 | 110 | NIL | - |  |  | -
20.12.24 | 8.45 | - |  | NIL | 668 | 448 | 200 | 122 | 78 | 110 | 6.4 | 142 | NIL | - |  |  | -
21.12.24 | 8.4 | - |  | NIL | 692 | 464 | 215 | 133 | 82 | 117 | 6.6 | 166 | 2 | - |  |  | -
23.12.24 | 8.5 | - |  | 0.1 | 731 | 490 | 240 | 148 | 92 | 142 | 6.8 | 183 | 5 | - |  |  | -
24.12.24 | 8.65 | - |  | NIL | 749 | 502 | 248 | 153 | 95 | 146 | 6.5 | 200 | 6 | - |  |  | -
25.12.24 | 8.6 | - |  | 0.2 | 768 | 515 | 240 | 148 | 92 | 150 | 6.4 | 210 | 5 | - |  |  | -
26.12.24 | 8.55 | - |  | 0.2 | 749 | 502 | 250 | 161 | 89 | 140 | 6.7 | 200 | 4 | - |  |  | -
27.12.24 | 8.5 | - |  | 0.3 | 764 | 512 | 254 | 160 | 94 | 142 | 6.2 | 204 | 4 | - |  |  | -
28.12.24 | 8.6 | - |  | 0.2 | 776 | 520 | 260 | 161 | 99 | 118 | 6.7 | 210 | 3 | - |  |  | -
30.12.24 | 8.5 | - |  | 0.1 | 813 | 545 | 245 | 151 | 94 | 125 | 6.9 | 230 | 4 | - |  |  | -
31.12.24 | 8.68 | - |  | 0.2 | 682 | 457 | 210 | 130 | 80 | 127 | 67 | 245 | 3 | - |  |  | -
01.01.25 | 8.8 | - |  | 0.2 | 701 | 470 | 217 | 137 | 80 | 136 | 6.9 | 260 | NIL | - |  |  | -
02.01.25 | 8.6 | - |  | 0.5 | 723 | 485 | 227 | 140 | 87 | 145 | 6.5 | 249 | 3 | - |  |  | -
03.01.25 | 8.65 | - |  | NIL | 701 | 470 | 236 | 146 | 90 | 150 | 6.2 | 240 | 4 | - |  |  | -
04.01.25 | 8.7 | - |  | NIL | 761 | 510 | 240 | 150 | 90 | 156 | 6.5 | 248 | 5 | - |  |  | -
08.01.25 | 8.6 | - |  | NIL | 850 | 470 | 250 | 155 | 95 | 110 | 5.5 | 200 | 3 | - |  |  | -
09.01.25 | 8.68 | - |  | NIL | 720 | 483 | 258 | 163 | 95 | 118 | 5 | 210 | 2 | - |  |  | -
10.01.25 | 8.8 | - |  | NIL | 731 | 490 | 264 | 170 | 94 | 120 | 4.5 | 208 | 6 | - |  |  | -
11.01.25 | 8.76 | - |  | NIL | 677 | 454 | 240 | 140 | 100 | 109 | 4 | 195 | 2 | - |  |  | -
13.01.25 | 8.56 | - |  | NIL | 776 | 520 | 310 | 190 | 120 | 140 | 3.5 | 175 | 2 | - |  |  | -
15.01.25 | 8.4 | - |  | 0.2 | 809 | 542 | 320 | 190 | 130 | 90 | 2.5 | 180 | 2 | - |  |  | -
16.01.25 | 8.55 | - |  | NIL | 826 | 554 | 327 | 202 | 125 | 98 | 2.5 | 195 | 5 | - |  |  | -
17.01.25 | 8.4 | - |  | 0.1 | 846 | 567 | 320 | 190 | 130 | 107 | 2.3 | 200 | 3 | - |  |  | -
18.01.25 | 8.4 | - |  | NIL | 865 | 580 | 300 | 186 | 114 | 90 | 2 | 170 | 3 | - |  |  | -
20.01.25 | 8.5 | - |  | NIL | 955 | 640 | 317 | 196 | 121 | 97 | 2 | 185 | 4 | - |  |  | -
21.01.25 | 8.65 | - |  | NIL | 886 | 593 | 320 | 198 | 122 | 107 | 1.6 | 190 |  | - |  |  | -
22.01.25 | 8.1 | - |  | NIL | 910 | 610 | 329 | 203 | 126 | 115 | 1.6 | 170 | 3 | - |  |  | -
23.01.25 | 8.25 | - |  | NIL | 935 | 627 | 341 | 211 | 130 | 110 | 1.3 | 155 | 3 | - |  |  | -
24.01.25 | 8.3 | - |  | NIL | 947 | 635 | 330 | 202 | 128 | 109 | 1 | 163 | 2 | - |  |  | -
25.01.25 | 8 | - |  | 0.2 | 916 | 614 | 290 | 166 | 124 | 95 | 1 | 134 |  | - |  |  | -
27.01.25 | 8.15 | - |  | NIL | 866 | 580 | 315 | 195 | 120 | 106 | 1 | 110 | NIL | - |  |  | -
28.01.25 | 8 | - |  | NIL | 883 | 592 | 329 | 203 | 126 | 110 | 1 | 98 | NIL
29.01.25 | 8.2 | - |  | 0.2 | 917 | 615 | 342 | 212 | 130 | 122 | 1 | 90 | 1 | - |  |  | -
30.01.25 | 8.1 | - |  | NIL | 895 | 600 | 325 | 201 | 124 | 110 | 1 | 78 | NIL
31.01.25 | 8.25 | - |  | 0.2 | 879 | 589 | 337 | 208 | 129 | 99 | 1 | 72 | 3
01.02.25 | 8.25 | - |  | 0.2 | 902 | 605 | 350 | 217 | 133 | 118 | 1 | 100 | 3 | - |  |  | -
03.02.25 | 8.4 | - |  | 3 | 885 | 593 | 308 | 200 | 108 | 112 |  | 110 | 2 | - |  |  | -
04.02.25 | 8.35 | - |  | 0.4 | 851 | 570 | 260 | 152 | 108 | 100 | 4 | 116 | 2 | - |  |  | -
05.02.25 | 8.42 | - |  | 0.3 | 848 | 568 | 234 | 140 | 94 | 119 | 3.9 | 120 | 4 | - |  |  | -
06.02.25 | 8.2 | - |  | 0.3 | 870 | 583 | 264 | 153 | 111 | 102 | 3 | 100 | NIL | - |  |  | -
07.02.25 | 8 | - |  | 0.3 | 882 | 590 | 273 | 159 | 114 | 100 | 2.8 | 94 | NIL | - |  |  | -
08.02.25 | 8 | - |  | 0.3 | 896 | 600 | 293 | 170 | 123 | 103 | 2 | 98 | NIL | - |  |  | -
10.02.25 | 8.08 | - |  | Nil | 909 | 609 | 303 | 178 | 125 | 100 | 2.1 | 96 | NIL | - |  |  | -
11.02.25 | 8.2 | - |  | 0.4 | 910 | 610 | 280 | 170 | 110 | 118 | 1 | 116 | NIL
12.02.25 | 8.2 | - |  | 0.2 | 880 | 590 | 295 | 182 | 113 | 118 | 1.4 | 110 | NIL
13.02.25 | 8.25 | - |  | 0.2 | 917 | 615 | 315 | 195 | 120 | 127 | 1.7 | 125 | 3
14.02.25 | 8.1 | - |  | 0.2 | 790 | 529 | 300 | 180 | 120 | 95 | 1 | 100 | NIL
15.02.25 | 8.2 | - |  | 0.3 | 855 | 573 | 293 | 173 | 120 | 92 | 2.3 | 93 | NIL
17.02.25 | 8.15 | - |  | Nil | 874 | 586 | 280 | 173 | 107 | 86 | 2.6 | 100 | NIL
18.02.25 | 8.1 | - |  | Nil | 850 | 570 | 265 | 164 | 101 | 80 | 2.8 | 100 | NIL
19.02.25 | 8.2 | - |  | Nil | 879 | 589 | 250 | 155 | 95 | 92 | 2.6 | 110 | 3
20.02.25 | 8.15 | - |  | Nil | 850 | 570 | 269 | 166 | 103 | 99 | 2.6 | 117 | 3
21.02.25 | 8.25 | - |  | 1 | 879 | 589 | 282 | 174 | 108 | 106 | 2.9 | 110 | 3
22.02.25 | 8.3 | - |  | Nil | 925 | 620 | 295 | 182 | 113 | 110 | 3.2 | 135 | 3
24.02.25 | 8.3 | - |  | 0.2 | 970 | 650 | 315 | 195 | 120 | 119 | 3 | 122 | 3
25.02.25 | 8.2 | - |  | Nil | 940 | 630 | 270 | 180 | 90 | 100 | 2.7 | 90 | 3
27.02.25 | 8.1 | - |  | Nil | 943 | 632 | 256 | 158 | 98 | 106 | 2.6 | 95 | 2
28.02.25 | 8 | - |  | Nil | 994 | 666 | 240 | 148 | 92 | 119 | 2.9 | 80 | NIL
01.03.25 | 8.1 | - |  | 0.2 | 955 | 640 | 285 | 176 | 109 | 125 | 2.7 | 100 | 2 | - |  |  | -
03.03.25 | 8.2 | - |  | 1 | 925 | 620 | 262 | 162 | 100 | 108 | 2.9 | 92 | 3 | - |  |  | -
04.03.25 | 8.2 | - |  | 0.2 | 962 | 645 | 280 | 173 | 107 | 100 | 2.6 | 100 | 2 | - |  |  | -
05.03.25 | 8 | - |  | NIL | 925 | 620 | 266 | 164 | 102 | 108 | 2.6 | 92 | NIL | - |  |  | -
06.03.25 | 8 | - |  | 0.2 | 960 | 643 | 250 | 155 | 95 | 80 | 2.7 | 86 | NIL | - |  |  | -
07.03.25 | 8.2 | - |  | 0.3 | 655 | 439 | 200 | 120 | 80 | 116 | 2.5 | 93 | NIL
08.03.25 | 8.1 | - |  | NIL | 671 | 450 | 219 | 135 | 84 | 127 | 2.3 | 100 | NIL
10.03.25 | 8 | - |  | NIL | 644 | 432 | 227 | 140 | 87 | 110 | 2.5 | 100 | NIL
11.03.25 | 8.2 | - |  | NIL | 629 | 420 | 210 | 128 | 82 | 112 | 2.6 | 110 | NIL
12.03.25 | 8.1 | - |  | NIL | 604 | 405 | 225 | 139 | 86 | 96 | 2.4 | 100 | NIL
13.03.25 | 8.25 | - |  | 0.5 | 701 | 470 | 215 | 133 | 82 | 99 | 2.6 | 122 | NIL
15.03.25 | 8.3 | - |  | NIL | 679 | 455 | 230 | 142 | 88 | 101 | 2.4 | 100 | 3
17.03.25 | 8.4 | - |  | 0.3 | 628 | 421 | 195 | 120 | 75 | 110 | 2.2 | 120 | 3
18.03.25 | 8.3 | - |  | 0.3 | 619 | 415 | 190 | 113 | 77 | 104 | 2.5 | 116 | 2
19.03.25 | 8.4 | - |  | 0.1 | 661 | 443 | 198 | 121 | 77 | 109 | 2.5 | 110 | 2
20.03.25 | 8.3 | - |  | NIL | 619 | 415 | 213 | 132 | 81 | 117 | 2.7 | 100 | NIL
21.03.25 | 8.4 | - |  | 0.1 | 639 | 428 | 205 | 127 | 78 | 102 | 2.4 | 107 | 3
22.03.25 | 8.4 | - |  | NIL | 650 | 436 | 219 | 135 | 84 | 110 | 2.4 | 119 | 2
24.03.25 | 8.2 | - |  | 0.2 | 635 | 421 | 200 | 122 | 78 | 107 | 2.6 | 120 | NIL
25.03.25 | 8.38 | - |  | 0.2 | 652 | 437 | 209 | 129 | 80 | 100 | 2.5 | 132 | 3
26.03.25 | 8.3 | - |  | 0.1 | 700 | 469 | 200 | 124 | 76 | 106 | 2.3 | 110 | 2
27.03.25 | 8.2 | - |  | NIL | 716 | 480 | 204 | 126 | 78 | 118 | 2.3 | 125 | NIL
28.03.25 | 8.37 | - |  | 0.2 | 722 | 484 | 210 | 126 | 84 | 110 | 2.5 | 129 | 3
29.03.25 | 8.4 | - |  | 0.3 | 698 | 480 | 205 | 123 | 82 | 106 | 2.9 | 100 | 3
31.03.25 | 8.15 | - |  | 0.1 | 696 | 479 | 200 | 120 | 80 | 104 | 2.7 | 95 | NIL
01.04.25 | 8.1 | - |  | NIL | 80 | 54 | 3 | 2 | 1 | 4 | - | 50 | - | - |  |  | -
02.04.25 | 8.1 | - |  | 0.2 | 704 | 472 | 215 | 133 | 82 | 109 | 2.9 | 103 | NIL | - |  |  | -
03.04.25 | 8 | - |  | 0.3 | 716 | 480 | 220 | 146 | 74 | 110 | 2.8 | 100 | NIL | - |  |  | -
04.04.25 | 8 | - |  | 0.2 | 742 | 497 | 220 | 134 | 86 | 112 | 2.7 | 95 | NIL | - |  |  | -
05.04.25 | 8.2 | - |  | 0.1 | 783 | 525 | 232 | 143 | 89 | 109 | 2.5 | 104 | 2 | - |  |  | -
07.04.25 | 8 | - |  | 0.1 | 794 | 532 | 200 | 120 | 80 | 120 | 2.4 | 90 | Nil | - |  |  | -
08.04.25 | 7.9 | - |  | 0.2 | 768 | 515 | 210 | 130 | 80 | 109 | 2.4 | 82 | NIL | - |  |  | -
09.04.25 | 8.2 | - |  | 0.2 | 782 | 524 | 207 | 128 | 79 | 119 | 2.5 | 90 | NIL | - |  |  | -
10.04.25 | 8.2 | - |  | 0.1 | 837 | 561 | 221 | 137 | 84 | 112 | 2.3 | 131 | NIL | - |  |  | -
11.04.25 | 8.2 | - |  | 0.1 | 859 | 576 | 214 | 132 | 82 | 107 | 2.3 | 92 | NIL | - |  |  | -
12.04.25 | 8.2 | - |  | 0.2 | 822 | 551 | 200 | 124 | 76 | 102 | 2.5 | 100 | NIL | - |  |  | -
14.04.25 | 8.2 | - |  | NIL | 822 | 551 | 207 | 128 | 79 | 97 | 2.3 | 105 | NIL | - |  |  | -
15.04.25 | 8.1 | - |  | 0.1 | 838 | 562 | 195 | 120 | 75 | 94 | 2.3 | 100 | NIL | - |  |  | -
16.04.25 | 8.1 | - |  | 0.2 | 862 | 578 | 203 | 124 | 79 | 90 | 2.5 | 100 | NIL | - |  |  | -
17.04.25 | 8.2 | - |  | NIL | 952 | 638 | 205 | 127 | 78 | 115 | 2.2 | 95 | NIL | - |  |  | -
18.04.25 | 8.25 | - |  | NIL | 910 | 610 | 213 | 132 | 81 | 109 | 2.4 | 98 | 2 | - |  |  | -
19.04.25 | 8.2 | - |  | NIL | 1026 | 688 | 218 | 139 | 79 | 118 | 3 | 85 | NIL | - |  |  | -
21.04.25 | 8.1 | - |  | NIL | 805 | 540 | 200 | 124 | 76 | 102 | 3.5 | 95 | NIL | - |  |  | -
22.04.25 | 8.1 | - |  | 0.1 | 828 | 555 | 195 | 120 | 75 | 98 | 3.5 | 95 | NIL | - |  |  | -
23.04.25 | 8.3 | - |  | 0.2 | 885 | 593 | 209 | 124 | 85 | 106 | 3.2 | 90 | NIL | - |  |  | -
24.04.25 | 8.2 | - |  | 0.2 | 817 | 548 | 240 | 148 | 92 | 185 | 3 | 100 | 1 | - |  |  | -
25.04.25 | 8.2 | - |  | 0.2 | 835 | 560 | 225 | 139 | 86 | 194 | 3 | 105 | 1 | - |  |  | -
26.04.25 | 8.2 | - |  | 0.3 | 804 | 539 | 240 | 148 | 92 | 213 | 3 | 100 | NIL | - |  |  | -
28.04.25 | 8.3 | - |  | 0.2 | 817 | 548 | 253 | 156 | 97 | 205 | 3 | 110 | 2 | - |  |  | -
29.04.25 | 8.25 | - |  | 0.1 | 841 | 564 | 240 | 148 | 92 | 230 | 2.5 | 90 | NIL | - |  |  | -
30.04.25 | 8.3 | - |  | 0.1 | 1014 | 680 | 228 | 141 | 87 | 242 | 2.5 | 96 | NIL | - |  |  | -
01.05.25 | 8.3 | - |  | 0.1 | 1002 | 672 | 235 | 145 | 90 | 234 | 2.5 | 90 | Nil | - |  |  | -
02.05.25 | 8.25 | - |  | NIL | 1037 | 695 | 210 | 130 | 80 | 210 | 2.5 | 90 | Nil | - |  |  | -
03.05.25 | 8.3 | - |  | 0.1 | 1048 | 699 | 215 | 139 | 76 | 212 | 2.3 | 95 | 2 | - |  |  | -
05.05.25 | 8.1 | - |  | 0.1 | 1080 | 720 | 200 | 124 | 76 | 220 | 2 | 91 | Nil | - |  |  | -
06.05.25 | 8.1 | - |  | 0.1 | 1010 | 676 | 190 | 117 | 73 | 198 | 2 | 100 | Nil | - |  |  | -
07.05.25 | 8.15 | - |  | NIL | 1029 | 690 | 196 | 121 | 75 | 190 | 2 | 96 | Nil | - |  |  | -
08.05.25 | 8 | - |  | 0.1 | 940 | 630 | 200 | 125 | 75 | 220 | 2.3 | 85 | Nil | - |  |  | -
09.05.25 | 8.1 | - |  | 0.1 | 958 | 642 | 210 | 130 | 80 | 226 | 2.3 | 89 | Nil | - |  |  | -
10.05.25 | 8.1 | - |  | 0.1 | 1028 | 688 | 210 | 130 | 80 | 218 | 2.5 | 84 | Nil | - |  |  | -
12.05.25 | 8.15 | - |  | 0.1 | 1000 | 670 | 200 | 124 | 76 | 210 | 2.3 | 90 | Nil | - |  |  | -
13.05.25 | 8.2 | - |  | NIL | 1020 | 684 | 205 | 133 | 72 | 214 | 2 | 96 | Nil | - |  |  | -
14.05.25 | 8.1 | - |  | 0.1 | 1000 | 670 | 190 | 117 | 73 | 205 | 2 | 90 | Nil | - |  |  | -
15.05.25 | 8.1 | - |  | 0.1 | 987 | 661 | 196 | 121 | 75 | 212 | 2.3 | 86 | Nil | - |  |  | -
16.05.25 | 8.2 | - |  | 0.2 | 1019 | 683 | 200 | 133 | 67 | 216 | 2 | 90 | Nil | - |  |  | -
17.05.25 | 8.15 | - |  | 0.1 | 1038 | 696 | 207 | 128 | 79 | 223 | 2 | 85 | Nil | - |  |  | -
19.05.25 | 8.3 | - |  | 0.1 | 970 | 649 | 200 | 124 | 76 | 220 | 2 | 84 | 2 | - |  |  | -
20.05.25 | 8.2 | - |  | 0.1 | 973 | 651 | 209 | 129 | 80 | 213 | 2.3 | 80 | Nil | - |  |  | -
21.05.25 | 8.1 | - |  | NIL | 886 | 593 | 169 | 99 | 70 | 235 | 2.3 | 60 | Nil | - |  |  | -
22.05.25 | 8.1 | - |  | NIL | 817 | 547 | 160 | 99 | 61 | 227 | 2 | 44 | Nil | - |  |  | -
23.05.25 | 8.15 | - |  | NIL | 790 | 529 | 152 | 83 | 69 | 225 | 2 | 50 | Nil | - |  |  | -
24.05.25 | 8 | - |  | NIL | 844 | 565 | 145 | 89 | 56 | 213 | 2 | 50 | Nil | - |  |  | -
26.05.25 | 7.6 | 19 |  | 0.5 | 759 | 508 | 120 | 74 | 46 | 177 | 2.2 | 54 | Nil | - |  |  | -
27.05.25 | 8.1 | - |  | NIL | 860 | 576 | 120 | 74 | 46 | 180 | 2.3 | 74 | Nil | - |  |  | -
28.05.25 | 8.2 | - |  | 0.1 | 854 | 572 | 127 | 78 | 49 | 205 | 2.5 | 74 | 1 | - |  |  | -
29.05.25 | 8.3 | - |  | 0.1 | 895 | 599 | 100 | 62 | 38 | 275 | 2.3 | 62 | Nil | - |  |  | -
30.05.25 | 8.2 | 22 |  | 0.5 | 941 | 630 | 110 | 68 | 42 | 228 | 2 | 95 | Nil | - |  |  | -
31.05.25 | 8.4 | 19 |  | 0.1 | 1029 | 689 | 160 | 99 | 61 | 260 | 2 | 100 | 2 | - |  |  | -
02.06.25 | 8.1 | 29 |  | 0.4 | 1168 | 782 | 210 | 130 | 80 | 293 | 2 | 75 | Nil | - |  |  | -
03.06.25 | 8.2 | 42 |  | NIL | 1182 | 791 | 200 | 124 | 76 | 275 | 2 | 80 | Nil | - |  |  | -
04.06.25 | 7.9 | 38 |  | 0.3 | 991 | 663 | 180 | 111 | 69 | 270 | 1.8 | 60 | Nil | - |  |  | -
05.06.25 | 7.9 | 32 |  | 0.2 | 988 | 661 | 169 | 104 | 65 | 265 | 1.8 | 54 | Nil | - |  |  | -
06.06.25 | 7.3 | 58 |  | 0.2 | 1065 | 713 | 193 | 119 | 74 | 284 | 1.5 | 50 | Nil | - |  |  | -
07.06.25 | 5.7 | 40 |  | 0.2 | 954 | 639 | 165 | 102 | 63 | 248 | 1.5 | 20 | Nil | - |  |  | -
09.06.25 | 8.2 | 52 |  | 0.5 | 1151 | 771 | 173 | 110 | 63 | 258 | 1.5 | 40 | Nil | - |  |  | -
10.06.25 | 8.1 | - |  | 0.2 | 1048 | 702 | 165 | 102 | 63 | 247 | 1.5 | 44 | Nil | - |  |  | -
11.06.25 | 8.2 | 45 |  | 0.4 | 1000 | 670 | 153 | 94 | 59 | 248 | 2 | 46 | Nil | - |  |  | -
12.06.25 | 8 | 71 | 44 | 0.2 | 1097 | 735 | 200 | 124 | 76 | 284 | 2.5 | 37 | Nil | - |  |  | -
13.06.25 | 7.7 | 66 | 40 | 0.3 | 1153 | 772 | 210 | 130 | 80 | 286 | 2.5 | 40 | Nil | - |  |  | -
14.06.25 | 8 | 69 | 47 | NIL | 1284 | 860 | 220 | 134 | 86 | 270 | 2.3 | 45 | Nil | - |  |  | -
16.06.25 | 8.4 | - | 27 | 0.1 | 1071 | 718 | 200 | 124 | 76 | 262 | 2.1 | 66 | Nil | - |  |  | -
17.06.25 | 8.4 | - | 22 | NIL | 978 | 655 | 180 | 111 | 69 | 248 | 1.8 | 70 | 2 | 0.4 |  |  | -
18.06.25 | 8.5 | - | 13 | NIL | 1000 | 670 | 195 | 120 | 75 | 260 | 2.1 | 66 | 3 | 0.4
19.06.25 | 8.5 | - | 12 | NIL | 953 | 638 | 200 | 124 | 76 | 240 | 2.5 | 50 | Nil | 0.3 |  |  | -
20.06.25 | 8.5 | - | 13 | NIL | 940 | 624 | 193 | 119 | 74 | 236 | 2.1 | 53 | Nil | 0.3 |  |  | -
21.06.25 | 8.4 | - | 14 | NIL | 900 | 603 | 160 | 99 | 61 | 236 | 2 | 66 | 2 | - |  |  | -
23.06.25 | 8.4 | - | 14 | NIL | 910 | 609 | 135 | 72 | 63 | 229 | 2 | 50 | Nil | 0.3 |  |  | -
24.06.25 | 8.3 | - | - | NIL | 815 | 546 | 115 | 71 | 44 | 213 | 2.2 | 62 | Nil | 0.3 |  |  | -
25.06.25 | 8.2 | - | 12 | NIL | 803 | 538 | 120 | 75 | 45 | 216 | 2 | 55 | Nil | 0.3 |  |  | -
26.06.25 | 8.1 | - | 19 | 0.2 | 889 | 596 | 110 | 68 | 42 | 220 | 1.9 | 52 | Nil | 0.3 |  |  | -
27.06.25 | 8 | - | - | NIL | 895 | 599 | 119 | 73 | 46 | 207 | 2.2 | 56 | Nil | 0.3 |  |  | -
28.06.25 | 7.9 | - | 18 | NIL | 830 | 556 | 120 | 74 | 46 | 213 | 2 | 33 | Nil | 0.3 |  |  | -
30.06.25 | 8.2 | - | 10 | NIL | 703 | 471 | 110 | 68 | 42 | 177 | 2.3 | 45 | Nil | 0.2 |  |  | -
01.07.25 | 8.2 | - | 11 | Nil | 668 | 471 | 121 | 75 | 46 | 185 | 2.3 | 45 | Nil | 0.2 |  |  | -
02.07.25 | 8.1 | - | 16 | Nil | 704 | 471 | 115 | 71 | 44 | 220 | 3 | 42 | Nil | 0.2 |  |  | -
03.07.25 | 8.2 | - | 18 | Nil | 725 | 485 | 110 | 68 | 42 | 200 | 3 | 50 | Nil | 0.2
04.07.25 | 8.2 | - | 23 | Nil | 774 | 518 | 100 | 62 | 38 | 213 | 2.7 | 50 | Nil | 0.3 |  |  | -
05.07.25 | 8.4 | - | 20 | Nil | 747 | 501 | 110 | 65 | 45 | 225 | 2.5 | 50 | 2 | 0.3 |  |  | -
07.07.25 | 8.5 | - | 15 | Nil | 701 | 469 | 120 | 74 | 46 | 213 | 2.5 | 66 | 3 | 0.3 |  |  | -
08.07.25 | 8.3 | - | 13 | Nil | 646 | 432 | 112 | 70 | 42 | 190 | 2.3 | 60 | 1 | 0.2 |  |  | -
09.07.25 | 8.4 | - | 10 | Nil | 610 | 408 | 120 | 74 | 46 | 210 | 2.3 | 50 | 2 | 0.2 |  |  | -
10.07.25 | 8.4 | - | 20 | Nil | 681 | 456 | 127 | 78 | 49 | 205 | 2 | 56 | 2 | 0.2
11.07.25 | 8.3 | - | 12 | Nil | 666 | 446 | 120 | 74 | 46 | 216 | 2 | 60 | Nil | 0.3
12.07.25 | 8.35 | - | 12 | Nil | 700 | 469 | 112 | 70 | 42 | 202 | 2.3 | 60 | 1 | 0.2
14.07.25 | 8.2 | - | - | Nil | 728 | 488 | 120 | 78 | 42 | 213 | 2 | 66 | Nil | 0.2
15.07.25 | 8.3 | - | 18 | Nil | 765 | 512 | 110 | 68 | 42 | 220 | 2 | 90 | Nil | 0.2
16.07.25 | 8.3 | - | - | 0.1 | 776 | 519 | 116 | 70 | 46 | 218 | 2.1 | 88 | Nil | 0.2
17.07.25 | 8.2 | - | 17 | Nil | 860 | 576 | 100 | 62 | 38 | 210 | 2 | 75 | Nil | 0.2
18.07.25 | 8.1 | - | 19 | Nil | 915 | 613 | 114 | 71 | 43 | 243 | 2.3 | 66 | Nil | 0.2
19.07.25 | 8.2 | - | 17 | Nil | 935 | 627 | 122 | 75 | 47 | 231 | 2.3 | 69 | Nil | 0.2
21.07.25 | 8.15 | - | 16 | Nil | 923 | 612 | 118 | 70 | 48 | 224 | 2.1 | 66 | Nil | 0.2
22.07.25 | 8.2 | - | - | Nil | 930 | 623 | 140 | 66 | 74 | 250 | 2 | 66 | Nil | 0.2
23.07.25 | 8.1 | - | - | Nil | 1164 | 780 | 125 | 77 | 48 | 225 | 2.3 | 58 | Nil | 0.2
24.07.25 | 8.1 | - | 18 | Nil | 1043 | 698 | 160 | 99 | 61 | 248 | 2.2 | 55 | Nil | 0.2
25.07.25 | 8.16 | - | 21 | Nil | 1067 | 715 | 148 | 91 | 57 | 238 | 2.1 | 57 | Nil | 0.2
26.07.25 | 8.25 | - | 20 | Nil | 1039 | 696 | 140 | 86 | 54 | 230 | 2 | 50 | Nil | 0.2
28.07.25 | 8.35 | - | 16 | Nil | 1098 | 736 | 120 | 74 | 46 | 284 | 2.2 | 75 | Nil | 0.2
29.07.25 | 8.3 | - | 17 | Nil | 1120 | 752 | 132 | 82 | 50 | 269 | 2 | 78 | Nil | 0.2
30.07.25 | 8.45 | - | 15 | Nil | 1192 | 798 | 146 | 90 | 56 | 270 | 2 | 80 | Nil | 0.2
31.07.25 | STOP
01.08.25 | STOP
02.08.25 | STOP
04.08.25 | STOP
05.08.25 | STOP
06.08.25 | STOP
07.08.25 | STOP
08.08.25 | 8.6 | - | 57 | NIL | 1136 | 761 | 110 | 62 | 48 | 388 | - | 80 | 2 | 0.4 |  |  | -
11.08.25 | 8.4 | - | 18 | NIL | 1254 | 840 | 100 | 62 | 38 | 340 | - | 50 |  | Nil |  |  | -
12.08.25 | 8.5 | - | 17 | NIL | 1270 | 850 | 119 | 74 | 45 | 290 | - | 62 | 2 | 0.2
13.08.25 | 8.4 | - | 18 | NIL | 1104 | 740 | 116 | 70 | 46 | 283 | - | 60 | 2 | 0.2
14.08.25 | 8.6 | - | 20 | NIL | 1574 | 1054 | 190 | 117 | 73 | 400 | - | 100 | 2 | 0.3
15.08.25 | 8.6 | - | 24 | NIL | 1402 | 980 | 200 | 124 | 76 | 396 | - | 105 | 2 | 0.3
18.08.25 | 8.8 | - | 34 | NIL | 1138 | 763 | 190 | 116 | 74 | 388 | - | 110 | 3 | 0.3
19.08.25 | 8.5 | - | 42 | NIL | 1134 | 760 | 215 | 133 | 82 | 380 | 2.2 | 105 | 2 | 0.3
20.08.25 | 8.7 | - | 44 | NIL | 1050 | 704 | 200 | 128 | 72 | 355 | 2.3 | 100 | 2 | 0.4
21.08.25 | 8.7 | - | 40 | NIL | 1230 | 825 | 205 | 127 | 78 | 284 | 1.9 | 102 | 2 | 0.3
22.08.25 | 8.6 | - | 38 | NIL | 1214 | 800 | 200 | 125 | 75 | 275 | 1.8 | 100 | 2 | 0.3
23.08.25 | 8.6 | - | - | NIL | 1100 | 737 | 210 | 130 | 80 | 260 | 2 | 105 | 2 | 0.3
26.08.25 | 8.63 | - | 39 | NIL | 851 | 570 | 190 | 118 | 72 | 248 | 2.1 | 82 | 2 | 0.3
27.08.25 | 8.7 | - | 22 | NIL | 740 | 495 | 162 | 100 | 62 | 182 | 1.7 | 72 | 2 | 0.3
28.08.25 | 8.35 | - | 19 | NIL | 761 | 510 | 174 | 108 | 66 | 177 | 1.6 | 80 | Nil | 0.3
29.08.25 | 8.35 | - | 19 | NIL | 730 | 489 | 155 | 100 | 55 | 213 | 1.6 | 100 | 2 | 0.3
0
0
0
| 5.7 | 17 |  | 0.1 | 80 | 54 | 3 | 2 | 0 | 142 | 5.8 | 20 | 1 | 0.2 | 0 | 0 | 0
MAX. | 9.4 | 28 |  | 3 | 1574 | 1054 | 545 | 337 | 513 | 400 | 10.5 | 390 | 10 | 0.4 | 0 | 0 | 0
AVG. | 8.3605 | 19 |  | 0.27087 | 909.9863 | 610.4456 | 252.0578 | 155.2774 | 96.8485 | 160.3356 | 4.1396 | 147.3503 | 0 | 0.25962
No. of < Spec | 9 | -- |  | 34 | -- | -- | -- | -- | -- | -- | 180 | -- | -- | -- | -- | -- | --
No. of > Spec | 251 | 15 |  | 7 | -- | 0 | 0 | -- | -- | 0 | 1 | 75 | -- | 0 | -- | 0 | 0
% < Specs. | 3.0612 | -- |  | 26.7717 | -- | -- | -- | -- | -- | -- | 63.1579 | [5 empty] | --
% > Specs. | 85.3741 | 21.7391 |  | 5.5118 |  | 0 | 0 |  | -- | 0 | 0.35088 | 25.5102 |  | 0