## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity |  | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU |  | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.04.23 | 8 | 82 |  | 0.6 | 2124 | 1423 | 773 | 433 | 340 | 213 | 7.2 | 113 | NIL | 0.3 | 82 | 910 | 136
02.04.23 | 8.3 | 85 |  | 0.4 | 3179 | 2130 | 1080 | 620 | 460 | 350 | 6.1 | 122 | NIL | 0.4 | 85 | 864 | 138
03.04.23 | 7.8 | 59 |  | 0 | 2210 | 1481 | 781 | 441 | 340 | 221 | 7.3 | 118 | NIL | 0.3 | 59 | 754 | 140
04.04.23 | 7.8 | 54 |  | 0 | 2210 | 1481 | 781 | 441 | 340 | 221 | 7.3 | 118 | NIL | 0.3 | 54 | 754 | 140
05.04.23 | 7.6 | 67 |  | 0.6 | 1982 | 1328 | 764 | 424 | 340 | 198 | 7.1 | 104 | NIL | 0.4 | 67 | 864 | 136
06.04.23 | 7.6 | 68 |  | 0.6 | 1940 | 1300 | 756 | 420 | 336 | 213 | 7.2 | 98 | NIL | 0.4 | 68 | 873 | 128
07.04.23 | 7.9 | 59 |  | 0 | 2149 | 1440 | 785 | 454 | 331 | 221 | 6.9 | 120 | NIL | 0.4 | 59 | 864 | 134
08.04.23 | 7.9 | 48 |  | 0.1 | 2090 | 1400 | 793 | 460 | 333 | 219 | 6.7 | 112 | NIL | 0.4 | 48 | 873 | 138
09.04.23 | 7.9 | 48 |  | 0.1 | 2090 | 1400 | 793 | 460 | 333 | 219 | 6.7 | 112 | NIL | 0.4 | 48 | 873 | 135
10.04.23 | 7.7 | 39 |  | 0.2 | 2030 | 1360 | 806 | 492 | 314 | 221 | 6.5 | 110 | NIL | 0.4 | 39 | 875 | 142
11.04.23 | 7.9 | 32 |  | 0 | 2060 | 1380 | 811 | 500 | 311 | 229 | 6.8 | 118 | NIL | 0.4 | 32 | 875 | 137
12.04.23 | 7.6 | 51 |  | 0.1 | 1985 | 1330 | 819 | 504 | 315 | 236 | 7 | 120 | NIL | 0.4 | 51 | 875 | 149
13.04.23 | 7.5 | 52 |  | 0.6 | 2283 | 1530 | 832 | 525 | 307 | 251 | 7.1 | 100 | NIL | 0.4 | 52 | 877 | 146
14.04.23 | 7.7 | 59 |  | 0.1 | 1821 | 1220 | 823 | 517 | 306 | 229 | 7 | 112 | NIL | 0.4 | 59 | 881 | 139
15.04.23 | 8.1 | 28 |  | 0.2 | 2318 | 1550 | 860 | 533 | 327 | 273 | 7.2 | 118 | NIL | 0.5 | 28 | 869 | 148
16.04.23 | 8.1 | 28 |  | 0.2 | 2318 | 1550 | 860 | 533 | 327 | 273 | 7.2 | 118 | NIL | 0.5 | 28 | 869 | 140
17.04.23 | 8 | 24 |  | 0.1 | 2283 | 1530 | 857 | 521 | 336 | 251 | 7 | 116 | NIL | 0.4 | 24 | 878 | 146
18.04.23 | 7.5 | 47 |  | 0.6 | 2297 | 1539 | 861 | 529 | 332 | 236 | 6.6 | 100 | NIL | 0.3 | 47 | 878 | 141
19.04.23 | 8.2 | 55 |  | 0.2 | 2236 | 1498 | 860 | 529 | 331 | 233 | 6.4 | 124 | NIL | 0.5 | 55 | 873 | 142
20.04.23 | 8.2 | 59 |  | 0 | 2228 | 1493 | 853 | 521 | 332 | 229 | 6 | 122 | NIL | 0.5 | 59 | 864 | 139
21.04.23 | 7.9 | 39 |  | 0.5 | 1866 | 1250 | 844 | 512 | 332 | 221 | 6.2 | 104 | NIL | 0.5 | 39 | 878 | 132
22.04.23 | 7.9 | 35 |  | 0.5 | 1881 | 1250 | 875 | 504 | 371 | 206 | 6.8 | 102 | NIL | 0.5 | 35 | 890 | 128
23.04.23 | 7.9 | 35 |  | 0.5 | 1881 | 1250 | 875 | 504 | 371 | 206 | 6.8 | 102 | NIL | 0.5 | 35 | 890 | 130
24.04.23 | 7.9 | 46 |  | 0.1 | 2298 | 1540 | 827 | 519 | 308 | 213 | 6.8 | 112 | NIL | 0.5 | 46 | 982 | 140
25.04.23 | 7.9 | 37 |  | 0.1 | 2373 | 1590 | 815 | 504 | 311 | 229 | 6.7 | 113 | NIL | 0.5 | 37 | 982 | 151
26.04.23 | 7.5 | 39 |  | 0.5 | 2267 | 1520 | 841 | 514 | 327 | 206 | 6.2 | 100 | NIL | 0.5 | 39 | 960 | 132
27.04.23 | 8.1 | 37 |  | 0.8 | 2403 | 1610 | 940 | 536 | 404 | 289 | 6 | 120 | NIL | 0.6 | 37 | 893 | 120
28.04.23 | 8.1 | 36 |  | 0.2 | 2527 | 1693 | 933 | 528 | 405 | 312 | 6 | 122 | NIL | 0.6 | 36 | 890 | 150
29.04.23 | 8 | 30 |  | 0 | 2269 | 1520 | 920 | 523 | 397 | 320 | 6.3 | 118 | NIL | 0.6 | 30 | 872 | 156
01.05.23 | 8.1 | 15 |  | 0.2 | 2574 | 1740 | 910 | 540 | 370 | 334 | 6 | 120 | NIL | 0.5 | 15 | 910 | 150
02.05.23 | 7.9 | 13 |  | 0.1 | 2537 | 1700 | 907 | 519 | 388 | 328 | 6.3 | 119 | NIL | 0.5 | 13 | 864 | 149
03.05.23 | 7.9 | 15 |  | 0.1 | 2310 | 1548 | 894 | 506 | 388 | 312 | 6.7 | 116 | NIL | 0.5 | 15 | 754 | 152
04.05.23 | 7.9 | 14 |  | 0 | 2490 | 1596 | 874 | 509 | 365 | 240 | 6 | 118 | NIL | 0.5 | 14 | 864 | 140
05.05.23 | 7.8 | 13 |  | 0 | 2507 | 1680 | 898 | 519 | 379 | 244 | 6.3 | 120 | NIL | 0.5 | 13 | 860 | 142
06.05.23 | 7.8 | 13 |  | 0 | 2364 | 1584 | 885 | 510 | 375 | 236 | 6 | 114 | NIL | 0.5 | 13 | 873 | 139
07.05.23 | 8.3 | 19 |  | 0 | 2373 | 1590 | 870 | 502 | 368 | 230 | 6.9 | 118 | NIL | 0.5 | 19 | 910 | 135
08.05.23 | 8.3 | 19 |  | 0 | 2373 | 1590 | 870 | 502 | 368 | 230 | 6.9 | 118 | NIL | 0.5 | 19 | 910 | 135
09.05.23 | 8.1 | 22 |  | 0.5 | 2634 | 1765 | 885 | 506 | 379 | 240 | 6 | 119 | NIL | 0.5 | 22 | 864 | 145
10.05.23 | 8.2 | 38 |  | 0.6 | 2507 | 1680 | 872 | 489 | 383 | 229 | 6.2 | 122 | NIL | 0.5 | 38 | 887 | 135
11.05.23 | 8.2 | 35 |  | 0.5 | 2671 | 1790 | 850 | 475 | 375 | 218 | 6.8 | 120 | NIL | 0.5 | 35 | 875 | 130
12.05.23 | 7.8 | 62 |  | 0.7 | 2432 | 1630 | 864 | 489 | 375 | 250 | 7.2 | 100 | NIL | 0.5 | 62 | 888 | 148
13.05.23 | 7.8 | 68 |  | 0.9 | 2463 | 1650 | 859 | 475 | 384 | 259 | 6.9 | 104 | NIL | 0.4 | 68 | 877 | 152
14.05.23 | 7.8 | 68 |  | 0.9 | 2463 | 1650 | 859 | 475 | 384 | 259 | 6.9 | 104 | NIL | 0.4 | 68 | 872 | 152
15.05.23 | 8 | 46 |  | 0.1 | 2284 | 1530 | 501 | 305 | 196 | 223 | 6.8 | 100 | NIL | 0.6 | 46 | 869 | 100
16.05.23 | 7.9 | 32 |  | 0.6 | 2254 | 1510 | 855 | 480 | 375 | 257 | 6.9 | 100 | NIL | 0.5 | 32 | 958 | 140
17.05.23 | 7.8 | 28 |  | 0.4 | 2149 | 1440 | 837 | 471 | 366 | 237 | 6.5 | 112 | NIL | 0.6 | 28 | 878 | 134
18.05.23 | 7.5 | 34 |  | 0.5 | 2403 | 1610 | 850 | 480 | 370 | 250 | 6.7 | 100 | NIL | 0.6 | 34 | 871 | 130
19.05.23 | 7.5 | 36 |  | 0.9 | 2373 | 1590 | 868 | 493 | 375 | 244 | 6 | 110 | NIL | 0.6 | 36 | 873 | 148
20.05.23 | 7.9 | 34 |  | 0.4 | 2522 | 1690 | 876 | 510 | 366 | 230 | 6.2 | 114 | NIL | 0.6 | 34 | 864 | 142
21.05.23 | 7.4 | 47 |  | 0.2 | 2237 | 1500 | 881 | 501 | 380 | 237 | 6 | 100 | NIL | 0.5 | 47 | 878 | 139
22.05.23 | 7.4 | 47 |  | 0.2 | 2237 | 1500 | 881 | 501 | 380 | 237 | 6 | 100 | NIL | 0.5 | 47 | 881 | 139
23.05.23 | 8 | 55 |  | 0.1 | 2462 | 1650 | 894 | 519 | 375 | 230 | 6.6 | 110 | NIL | 0.5 | 55 | 984 | 145
24.05.23 | 7.8 | 40 |  | 0 | 2179 | 1460 | 885 | 510 | 375 | 226 | 6.9 | 114 | NIL | 0.5 | 40 | 982 | 140
25.05.23 | 7.9 | 39 |  | 0 | 2194 | 1470 | 920 | 523 | 397 | 244 | 7 | 118 | NIL | 0.5 | 39 | 875 | 137
26.05.23 | 7.5 | 26 |  | 0 | 2254 | 1510 | 907 | 514 | 393 | 237 | 6.8 | 110 | NIL | 0.5 | 26 | 960 | 147
27.05.23 | 8 | 26 |  | 0.2 | 2223 | 1490 | 911 | 532 | 379 | 316 | 7.2 | 120 | NIL | 0.5 | 26 | 893 | 156
28.05.23 | 8 | 26 |  | 0.2 | 2223 | 1490 | 911 | 532 | 379 | 316 | 7.2 | 120 | NIL | 0.5 | 26 | 888 | 156
29.05.23 | 7.5 | 22 |  | 0.6 | 2149 | 1440 | 894 | 506 | 388 | 230 | 6.9 | 112 | NIL | 0.5 | 22 | 872 | 140
30.05.23 | 7.7 | 30 |  | 0.6 | 2090 | 1400 | 881 | 492 | 389 | 223 | 6.4 | 100 | NIL | 0.5 | 30 | 893 | 137
31.05.23 | 7.6 | 33 |  | 0.5 | 2074 | 1390 | 873 | 480 | 393 | 220 | 6.2 | 112 | NIL | 0.5 | 33 | 890 | 132
01.06.23 | 7.5 | 24 |  | 0.5 | 2047 | 1370 | 872 | 484 | 388 | 230 | 6.5 | 100 | NIL | 0.5 | 24 | 910 | 142
02.06.23 | 7.6 | 35 |  | 0 | 1940 | 1300 | 859 | 475 | 384 | 223 | 6.3 | 110 | NIL | 0.5 | 35 | 864 | 139
03.06.23 | 7.9 | 37 |  | 0 | 2000 | 1340 | 870 | 480 | 390 | 230 | 6.9 | 118 | NIL | 0.5 | 37 | 754 | 140
04.06.23 | 7.9 | 37 |  | 0 | 2000 | 1340 | 870 | 480 | 390 | 230 | 6.9 | 118 | NIL | 0.5 | 37 | 864 | 140
05.06.23 | 8 | 39 |  | 0.5 | 1492 | 1000 | 560 | 329 | 231 | 226 | 6.2 | 114 | NIL | 0.5 | 39 | 860 | 120
06.06.23 | 7.8 | 37 |  | 0.1 | 1350 | 905 | 517 | 315 | 202 | 230 | 6.5 | 120 | NIL | 0.4 | 37 | 873 | 122
07.06.23 | 8 | 35 |  | 0 | 1257 | 854 | 562 | 352 | 210 | 202 | 7 | 118 | NIL | 0.4 | 35 | 910 | 125
08.06.23 | 7.9 | 27 |  | 0 | 1704 | 1142 | 549 | 344 | 205 | 200 | 6.5 | 120 | NIL | 0.4 | 27 | 910 | 133
09.06.23 | 7.8 | 25 |  | 0 | 1737 | 1164 | 530 | 337 | 193 | 204 | 6.9 | 116 | NIL | 0.4 | 25 | 864 | 130
10.06.23 | 7.7 | 24 |  | 0 | 1750 | 1173 | 542 | 340 | 202 | 208 | 6 | 112 | NIL | 0.4 | 24 | 887 | 133
11.06.23 | 7.7 | 22 |  | 0 | 1750 | 1173 | 542 | 340 | 202 | 208 | 6 | 112 | NIL | 0.4 | 22 | 875 | 130
12.06.23 | 7.7 | 24 |  | 0 | 1552 | 1040 | 541 | 340 | 201 | 236 | 7.2 | 100 | NIL | 0.3 | 24 | 888 | 145
13.06.23 | 7.6 | 23 |  | 0 | 1611 | 1080 | 558 | 349 | 209 | 243 | 7.5 | 118 | NIL | 0.3 | 23 | 877 | 150
14.06.23 | 7.8 | 24 |  | 0.2 | 1573 | 1054 | 567 | 358 | 209 | 257 | 7 | 104 | NIL | 0.3 | 24 | 872 | 142
15.06.23 | 7.6 | 30 |  | 0.1 | 1950 | 1293 | 593 | 359 | 234 | 218 | 6.9 | 95 | NIL | 0.3 | 30 | 869 | 132
16.06.23 | 7.4 | 31 |  | 0.2 | 1966 | 1317 | 584 | 344 | 240 | 221 | 6 | 100 | NIL | 0.3 | 31 | 958 | 137
17.06.23 | 7.5 | 28 |  | 0.2 | 1952 | 1310 | 562 | 339 | 223 | 218 | 7 | 98 | NIL | 0.4 | 28 | 878 | 130
18.06.23 | 7.5 | 25 |  | 0.2 | 1952 | 1310 | 562 | 339 | 223 | 218 | 7 | 98 | NIL | 0.4 | 25 | 871 | 130
19.06.23 | 7.5 | 41 |  | 0 | 2000 | 1340 | 606 | 344 | 262 | 214 | 7 | 95 | NIL | 0.3 | 41 | 873 | 128
20.06.23 | 7.3 | 30 |  | 0.1 | 1630 | 1092 | 637 | 388 | 249 | 236 | 7.1 | 92 | NIL | 0.3 | 30 | 864 | 146
21.06.23 | 7.6 | 28 |  | 0 | 1896 | 1270 | 615 | 358 | 257 | 214 | 6.8 | 100 | NIL | 0.5 | 28 | 878 | 138
22.06.23 | 7.2 | 25 |  | 0.1 | 1955 | 1310 | 623 | 344 | 279 | 243 | 6.5 | 96 | NIL | 0.5 | 25 | 881 | 140
23.06.23 | 7.3 | 28 |  | 0.1 | 2462 | 1650 | 894 | 519 | 375 | 230 | 6.6 | 110 | NIL | 0.5 | 55 | 984 | 145
24.06.23 | 7.6 | 37 |  | 0.3 | 1640 | 1093 | 589 | 348 | 241 | 240 | 6.5 | 92 | NIL | 0.6 | 37 | 982 | 130
25.06.23 | 7.6 | 33 |  | 0.3 | 1640 | 1093 | 589 | 348 | 241 | 240 | 6.5 | 92 | NIL | 0.6 | 33 | 875 | 137
26.06.23 | 7.7 | 35 |  | 0.1 | 1655 | 1109 | 579 | 351 | 228 | 243 | 6.7 | 89 | NIL | 0.7 | 35 | 960 | 139
27.06.23 | 7.1 | 30 |  | 0.1 | 1916 | 1284 | 612 | 345 | 267 | 237 | 5.9 | 90 | NIL | 0.7 | 30 | 893 | 141
28.06.23 | 7.4 | 28 |  | 0 | 1671 | 1120 | 603 | 242 | 361 | 229 | 6.3 | 82 | NIL | 0.8 | 28 | 888 | 146
29.06.23 | 7.6 | 27 |  | 0.1 | 1851 | 1240 | 621 | 351 | 270 | 243 | 6.9 | 84 | NIL | 0.8 | 27 | 872 | 151
30.06.23 | 7.7 | 28 |  | 0.1 | 1895 | 1270 | 634 | 369 | 265 | 240 | 7 | 90 | NIL | 0.8 | 28 | 893 | 146
01.07.23 | 7.6 | 17 |  | 0.1 | 1940 | 1300 | 600 | 340 | 260 | 240 | 6.2 | 91 | NIL | 0.5 | 17 | 910 | 134
02.07.23 | 7.6 | 17 |  | 0 | 1940 | 1300 | 600 | 340 | 260 | 240 | 6.2 | 91 | NIL | 0.5 | 17 | 864 | 139
03.07.23 | 7.8 | 19 |  | 0 | 1865 | 1250 | 612 | 351 | 261 | 243 | 6.5 | 96 | NIL | 0.8 | 19 | 754 | 140
04.07.23 | 7.4 | 20 |  | 0.3 | 2213 | 1453 | 642 | 368 | 274 | 257 | 6.8 | 100 | NIL | 0.8 | 20 | 864 | 159
06.07.23 | 7.5 | 28 |  | 0 | 2000 | 1340 | 625 | 342 | 283 | 271 | 7 | 102 | NIL | 0.7 | 28 | 873 | 152
07.07.23 | 7 | 70 |  | 0 | 2373 | 1590 | 642 | 355 | 287 | 279 | 6.5 | 87 | NIL | 0.7 | 70 | 910 | 157
09.07.23 | 7.9 | 27 |  | 0 | 1704 | 1142 | 549 | 344 | 205 | 200 | 6.5 | 120 | NIL | 0.4 | 27 | 864 | 130
10.07.23 | 7.5 | 26 |  | 0 | 2313 | 1550 | 702 | 377 | 325 | 216 | 7.5 | 90 | NIL | 0.7 | 26 | 887 | 169
11.07.23 | 7.3 | 20 |  | 0 | 2246 | 1504 | 693 | 364 | 329 | 321 | 6.2 | 94 | NIL | 0.7 | 20 | 875 | 136
12.07.23 | 7.6 | 30 |  | 0.5 | 1963 | 1315 | 689 | 372 | 317 | 293 | 7.2 | 97 | NIL | 0.7 | 30 | 888 | 162
13.07.23 | 7.9 | 28 |  | 0 | 1970 | 1320 | 678 | 364 | 314 | 290 | 6.9 | 98 | NIL | 0.7 | 28 | 877 | 153
14.07.23 | 7.6 | 24 |  | 0 | 2239 | 1500 | 693 | 364 | 329 | 286 | 6.7 | 100 | NIL | 0.7 | 24 | 872 | 159
15.07.23 | 7.6 | 24 |  | 0 | 2015 | 1350 | 685 | 360 | 325 | 270 | 7 | 98 | NIL | 0.7 | 24 | 869 | 152
16.07.23 | 7.6 | 24 |  | 0 | 2015 | 1350 | 685 | 360 | 325 | 270 | 7 | 98 | NIL | 0.7 | 24 | 958 | 158
17.07.23 | 7.7 | 20 |  | 0 | 1970 | 1320 | 690 | 355 | 335 | 250 | 6.8 | 100 | NIL | 0.7 | 20 | 878 | 167
18.07.23 | 7.8 | 30 |  | 0.3 | 2134 | 1430 | 706 | 351 | 355 | 264 | 6.9 | 98 | NIL | 0.7 | 30 | 871 | 158
19.07.23 | 7.3 | 37 |  | 0.3 | 2090 | 1400 | 687 | 342 | 345 | 243 | 7 | 90 | NIL | 0.7 | 37 | 873 | 153
20.07.23 | 7.7 | 40 |  | 0.3 | 1940 | 1300 | 710 | 364 | 346 | 279 | 6.9 | 100 | NIL | 0.7 | 40 | 864 | 161
21.07.23 | 7.6 | 39 |  | 0 | 1910 | 1280 | 676 | 351 | 325 | 271 | 6 | 96 | NIL | 0.7 | 39 | 878 | 150
23.07.23 | 7.2 | 25 |  | 0.1 | 1955 | 1310 | 623 | 344 | 279 | 243 | 6.5 | 96 | NIL | 0.5 | 25 | 984 | 145
24.07.23 | 7.5 | 20 |  | 0 | 1627 | 1090 | 710 | 368 | 342 | 271 | 5.9 | 102 | NIL | 0.6 | 20 | 882 | 146
25.07.23 | 7.4 | 21 |  | 0 | 1522 | 1020 | 698 | 372 | 326 | 300 | 6.2 | 102 | NIL | 0.5 | 21 | 875 | 149
26.07.23 | 7.4 | 22 |  | 0 | 1403 | 940 | 706 | 364 | 342 | 290 | 5.9 | 87 | NIL | 0.5 | 22 | 960 | 152
27.07.23 | 7.3 | 21 |  | 0 | 1487 | 966 | 681 | 342 | 339 | 279 | 6.3 | 92 | NIL | 0.5 | 21 | 893 | 140
28.07.23 | 7.7 | 20 |  | 0.1 | 1343 | 900 | 648 | 300 | 348 | 254 | 6.9 | 104 | NIL | 0.5 | 20 | 888 | 134
29.07.23 | 7.9 | 18 |  | 0.1 | 1333 | 893 | 659 | 312 | 347 | 257 | 6.2 | 100 | NIL | 0.5 | 18 | 872 | 136
30.07.23 | 7.9 | 18 |  | 0.1 | 1333 | 893 | 659 | 312 | 347 | 257 | 6.2 | 100 | NIL | 0.5 | 18 | 886 | 149
31.07.23 | 7.5 | 48 |  | 0.1 | 1636 | 1096 | 668 | 321 | 347 | 272 | 6.1 | 104 | NIL | 0.5 | 48 | 893 | 139
01.08.23 | 7.4 | 59 |  | 0.1 | 1676 | 1123 | 650 | 315 | 335 | 264 | 6 | 100 | NIL | 0.5 | 59 | 910 | 135
02.05.23 | 7.9 | 13 |  | 0.1 | 2537 | 1700 | 907 | 519 | 388 | 328 | 6.3 | 119 | NIL | 0.5 | 13 | 864 | 149
03.05.23 | 7.9 | 15 |  | 0.1 | 2310 | 1548 | 894 | 506 | 388 | 312 | 6.7 | 116 | NIL | 0.5 | 15 | 754 | 152
04.08.23 | 7.5 | 40 |  | 0.1 | 2075 | 1390 | 643 | 325 | 318 | 282 | 6.5 | 104 | NIL | 0.6 | 40 | 864 | 142
05.08.23 | 7.4 | 38 |  | 0 | 2119 | 1420 | 691 | 360 | 331 | 272 | 6.8 | 110 | NIL | 0.6 | 38 | 860 | 136
06.08.23 | 7.8 | 13 |  | 0 | 2364 | 1584 | 885 | 510 | 375 | 236 | 6 | 114 | NIL | 0.5 | 13 | 873 | 139
07.08.23 | 7.8 | 25 |  | 0 | 2268 | 1520 | 703 | 366 | 337 | 286 | 6.2 | 113 | NIL | 0.6 | 25 | 910 | 152
08.08.23 | 7.8 | 22 |  | 0.1 | 2313 | 1550 | 698 | 360 | 338 | 275 | 6 | 102 | NIL | 0.6 | 22 | 910 | 148
09.08.23 | 7.9 | 26 |  | 0 | 2372 | 1589 | 815 | 437 | 378 | 398 | 6.7 | 110 | NIL | 0.6 | 26 | 864 | 154
10.08.23 | 7.2 | 25 |  | 0 | 2373 | 1590 | 824 | 445 | 379 | 433 | 7 | 112 | NIL | 0.6 | 25 | 887 | 158
11.08.23 | 7.6 | 28 |  | 0 | 2376 | 1592 | 818 | 440 | 378 | 438 | 6.9 | 118 | NIL | 0.6 | 28 | 875 | 150
12.08.23 | 7.6 | 24 |  | 0 | 2448 | 1640 | 820 | 399 | 421 | 391 | 6.5 | 100 | NIL | 0.6 | 24 | 888 | 140
13.08.23 | 7.8 | 68 |  | 0.9 | 2463 | 1650 | 859 | 475 | 384 | 259 | 6.9 | 104 | NIL | 0.4 | 68 | 877 | 152
14.08.23 | 7.514 | 14 |  | 0 | 2507 | 1680 | 832 | 480 | 352 | 400 | 6.2 | 104 | NIL | 0.6 | 14 | 872 | 144
15.08.23 | 7.4 | 15 |  | 0 | 2573 | 1700 | 793 | 472 | 321 | 410 | 6.4 | 116 | NIL | 0.6 | 15 | 869 | 150
16.08.23 | 6.9 | 23 |  | 0.3 | 2229 | 1494 | 800 | 484 | 316 | 424 | 6.9 | 113 | NIL | 0.6 | 23 | 958 | 155
17.08.23 | 7.1 | 36 |  | 0.1 | 2149 | 1440 | 843 | 496 | 347 | 440 | 7 | 104 | NIL | 0.6 | 36 | 878 | 157
18.08.23 | 7.8 | 31 |  | 0.6 | 2209 | 1430 | 835 | 389 | 446 | 398 | 6.9 | 114 | NIL | 0.6 | 31 | 871 | 141
19.08.23 | 7.4 | 40 |  | 0 | 2074 | 1390 | 822 | 411 | 411 | 384 | 7 | 98 | NIL | 0.6 | 40 | 873 | 138
20.05.23 | 7.9 | 34 |  | 0.4 | 2522 | 1690 | 876 | 510 | 366 | 230 | 6.2 | 114 | NIL | 0.6 | 34 | 864 | 142
21.08.23 | 8.2 | 20 |  | 0.1 | 2223 | 1489 | 829 | 418 | 411 | 387 | 6.4 | 99 | NIL | 0.6 | 20 | 878 | 134
22.05.23 | 7.4 | 47 |  | 0.2 | 2237 | 1500 | 881 | 501 | 380 | 237 | 6 | 100 | NIL | 0.5 | 47 | 881 | 139
23.05.23 | 8 | 55 |  | 0.1 | 2462 | 1650 | 894 | 519 | 375 | 230 | 6.6 | 110 | NIL | 0.5 | 55 | 984 | 145
24.05.23 | 7.8 | 40 |  | 0 | 2179 | 1460 | 885 | 510 | 375 | 226 | 6.9 | 114 | NIL | 0.5 | 40 | 982 | 140
25.08.23 | 7.2 | 25 |  | 0.2 | 2209 | 1480 | 818 | 450 | 368 | 412 | 6.9 | 110 | NIL | 0.6 | 25 | 875 | 138
26.05.23 | 7.5 | 26 |  | 0 | 2254 | 1510 | 907 | 514 | 393 | 237 | 6.8 | 110 | NIL | 0.5 | 26 | 960 | 147
27.05.23 | 8 | 26 |  | 0.2 | 2223 | 1490 | 911 | 532 | 379 | 316 | 7.2 | 120 | NIL | 0.5 | 26 | 893 | 156
28.05.23 | 8 | 26 |  | 0.2 | 2223 | 1490 | 911 | 532 | 379 | 316 | 7.2 | 120 | NIL | 0.5 | 26 | 888 | 156
29.08.23 | 7.6 | 15 |  | 0.1 | 2119 | 1420 | 794 | 433 | 361 | 405 | 5.9 | 100 | NIL | 0.5 | 15 | 872 | 139
30.08.23 | 7.7 | 30 |  | 0.6 | 2090 | 1400 | 881 | 492 | 389 | 223 | 6.4 | 100 | NIL | 0.5 | 30 | 893 | 137
31.08.23 | 7.6 | 33 |  | 0.5 | 2074 | 1390 | 873 | 480 | 393 | 220 | 6.2 | 112 | NIL | 0.5 | 33 | 890 | 132
01.09.23 | 7.35 | 33 |  | 0.4 | 2104 | 1410 | 735 | 386 | 349 | 355 | 6.9 | - | NIL | 0.7 |  |  | 166
2023-09-02 | 7.72 | 56 |  | 0.4 | 2037 | 1365 | 748 | 399 | 349 | 369 | 7.1 | 102 | NIL | 0.7 |  |  | 172
2023-09-04 | 7.56 | 21 |  | 0.3 | 1731 | 1160 | 617 | 314 | 303 | 282 | 5.9 | 110 | NIL | 0.5 |  |  | 121
2023-09-05 | 7.72 | 42 |  | NIL | 2701 | 1810 | 760 | 399 | 361 | 398 | 7.3 | - | NIL | 0.7 |  |  | 188
2023-09-06 | 7.36 | 32 |  | NIL | 2173 | 1456 | 718 | 365 | 353 | 291 | 7.1 | - | NIL | 0.7 |  |  | 181
2023-09-07 | 7.8 | 25 |  | NIL | 2294 | 1540 | 760 | 372 | 388 | 390 | 6.4 | - | NIL | 0.6 |  |  | 180
2023-09-08 | 7.73 | 26 |  | NIL | 2268 | 1520 | 714 | 357 | 357 | 398 | 6.5 | - | NIL | 0.7 |  |  | 184
2023-09-09 | 7.69 | 22 |  | NIL | 2074 | 1390 | 733 | 369 | 364 | 391 | 6.2 | - | NIL | 0.7 |  |  | 188
2023-09-11 | 6.92 | 16 |  | NIL | 2240 | 1501 | 757 | 365 | 392 | 391 | 6.4 | - | NIL | 0.6 |  |  | 179
2023-09-12 | 7.45 | 20 |  | NIL | 2209 | 1480 | 768 | 372 | 396 | 398 | 6 | - | NIL | 0.6 |  |  | 189
2023-09-13 | 7.41 | 17 |  | NIL | 2365 | 1585 | 760 | 376 | 384 | 405 | 6.2 | - | NIL | 0.7 |  |  | 182
2023-09-14 | 7.81 | 21 |  | 0.2 | 2011 | 1348 | 768 | 365 | 403 | 383 | 6.1 | - | NIL | 0.6 |  |  | 174
2023-09-15 | 7.72 | 24 |  | 0.3 | 2150 | 1427 | 776 | 396 | 380 | 376 | 6 | - | NIL | 0.6 |  |  | 179
2023-09-16 | 7.13 | 20 |  | 0.6 | 1940 | 1300 | 768 | 380 | 388 | 391 | 5.8 | - | NIL | 0.7 |  |  | 193
2023-09-18 | 7.56 | 20 |  | 0.3 | 1985 | 1330 | 811 | 384 | 427 | 362 | 5.1 | - | NIL | 0.7 |  |  | 193
2023-09-19 | 7.64 | 22 |  | 0.2 | 2020 | 1350 | 820 | 390 | 430 | 354 | 5.3 | - | NIL | 0.7 |  |  | 187
2023-09-20 | 7.24 | 30 |  | 0.7 | 1703 | 1141 | 795 | 392 | 403 | 369 | 5.3 | - | NIL | 0.7 |  |  | 189
2023-09-21 | 7.25 | 41 |  | 0.6 | 1752 | 1174 | 803 | 376 | 427 | 376 | 5.6 |  | NIL | 0.6 |  |  | 178
2023-09-22 | 7.28 | 42 |  | 0.7 | 1731 | 1160 | 799 | 380 | 419 | 369 | 5.2 | - | NIL | 0.6 |  |  | 182
2023-09-23 | 7.4 | 41 |  | NIL | 1789 | 1199 | 795 | 388 | 407 | 362 | 5.4 | - | NIL | 0.6 |  |  | 188
2023-09-25 | 7.56 | 38 |  | NIL | 1686 | 1130 | 757 | 369 | 388 | 311 | 5 | - | NIL | 0.6 |  |  | 163
2023-09-26 | 7.44 | 42 |  | 0.4 | 1564 | 1048 | 764 | 376 | 388 | 347 | 5.1 | - | NIL | 0.6 |  |  | 178
2023-09-27 | 7.74 | 45 |  | 0.7 | 1583 | 1061 | 784 | 384 | 400 | 369 | 5.3 | - | NIL | 0.6 |  |  | 186
2023-09-29 | 7.12 | 61 |  | 0.8 | 1957 | 1311 | 792 | 392 | 400 | 376 | 5.2 | - | NIL | 0.7 |  |  | 172
2023-09-30 | 7.21 | 59 |  | 0.6 | 2064 | 1383 | 795 | 380 | 415 | 362 | 5.1 | - | NIL | 0.6 |  |  | 178
2023-11-01 | 7.83 | 21 |  | - | 2093 | 1401 | 823 | 312 | 511 | 266 | 3.1 | - | NIL | 0.7 |  |  | 158
2023-11-02 | 7.84 | 61 |  | NIL | 2181 | 1558 | 809 | 303 | 506 | 280 | 3.3 | - | NIL | 0.6 |  |  | 162
03.11.23 | 7.67 | 21 |  | NIL | 2131 | 1428 | 777 | 402 | 375 | 287 | 3.5 | - | NIL | 0.5 |  |  | 158
2023-11-04 | 7.7 | 26 |  | NIL | 1962 | 1315 | 818 | 378 | 440 | 311 | 3.8 | - | NIL | 0.5 |  |  | 186
2023-11-06 | 7.76 | 35 |  | NIL | 2015 | 1350 | 840 | 383 | 457 | 282 | 3.5 | - | NIL | 0.5 |  |  | 181
2023-11-07 | 7.9 | 22 |  | NIL | 1963 | 1315 | 845 | 378 | 467 | 275 | 3.4 | - | NIL | 0.5 |  |  | 188
2023-11-08 | 7.26 | 33 |  | NIL | 2119 | 1420 | 849 | 365 | 484 | 260 | 3.3 | - | NIL | 0.5 |  |  | 175
2023-11-09 | 7.88 | 19 |  | NIL | 1954 | 1309 | 858 | 378 | 480 | 282 | 3.5 | - | NIL | 0.5 |  |  | 179
2023-11-10 | 7.5 | 46 |  | 0.7 | 1934 | 1296 | 836 | 453 | 383 | 289 | 3.3 | - | NIL | 0.5 |  |  | 162
11.11.23 | 7.4 | 69 |  | NIL | 2034 | 1363 | 836 | 453 | 383 | 246 | 3.5 | - | NIL | - |  |  | 152
2023-11-17 | 7.67 | 30 |  | NIL | 1410 | 945 | 827 | 427 | 400 | 253 | 3.5 | - | NIL | 0.5 |  |  | 144
2023-11-21 | 7.33 | 22 |  | NIL | 1381 | 925 | 827 | 440 | 387 | 253 | 3.1 | - | NIL | 0.5 |  |  | 141
2023-11-22 | 7.11 | 41 |  | NIL | 1204 | 790 | 818 | 444 | 374 | 239 | 2.9 | - | NIL | 0.5 |  |  | 139
2023-11-23 | 7.29 | 24 |  | NIL | 1037 | 695 | 858 | 449 | 409 | 246 | 3.2 | - | NIL | 0.5 |  |  | 246
2023-11-24 | 7.99 | 59 |  | NIL | 919 | 616 | 937 | 532 | 405 | 224 | 3.2 | - | NIL | 0.5 |  |  | 124
2023-11-28 | 7.58 | 86 |  | NIL | 1210 | 811 | 968 | 524 | 444 | 253 | 3.4 | - | NIL | 0.5 |  |  | 149
2023-11-29 | 7.75 | 115 |  | NIL | 1260 | 844 | 950 | 532 | 418 | 239 | 3.1 | - | NIL | 0.5 |  |  | 141
2023-11-30 | 7.45 | 70 |  | NIL | 2054 | 1376 | 968 | 541 | 427 | 231 | 3.3 | - | NIL | 0.5 |  |  | 145
2023-12-01 | 7.38 | 79 |  | NIL | 1934 | 1296 | 1082 | 629 | 453 | 217 | 3.8 | - | NIL | 0.5 |  |  | 138
2023-12-02 | 7.42 | 50 |  | NIL | 2054 | 1376 | 1008 | 576 | 432 | 246 | 4.2 | - | NIL | 0.5 |  |  | 143
2023-12-04 | 8.19 | 29 |  | NIL | 2239 | 1500 | 999 | 550 | 449 | 224 | 4.1 | - | NIL | 0.5 |  |  | 160
2023-12-06 | 7.12 | 54 |  | 0.9 | 1982 | 1328 | 1047 | 590 | 457 | 231 | 4 | - | NIL | 0.5 |  |  | 133
2023-12-14 | 7.21 | 32 |  | 0.6 | 1820 | 1220 | 950 | 537 | 413 | 244 | 4.4 | - | NIL | 0.5 |  |  | 151
2023-12-15 | 7.09 | 40 |  | 0.5 | 1715 | 1176 | 937 | 546 | 391 | 252 | 4.2 | - | NIL | 0.5 |  |  | 148
2023-12-16 | 7.46 | 45 |  | 0.5 | 1910 | 1280 | 928 | 537 | 391 | 244 | 4.3 | - | NIL | 0.5 |  |  | 150
2023-12-18 | 7.1 | 46 |  | 0.3 | 1611 | 1080 | 937 | 48 | 889 | 289 | 4 | - | NIL | 0.5 |  |  | 139
2023-12-19 | 7.56 | 49 |  | NIL | 1432 | 960 | 929 | 575 | 354 | 259 | 3.7 | - | NIL | 0.5 |  |  | 88
2023-12-19 | 7.4 | 50 |  | 0.8 | 1507 | 1010 | 1035 | 731 | 304 | 289 | 3.8 | - | NIL | 0.5 |  |  | 142
2023-12-20 | 7.2 | 70 |  | 0.9 | 1478 | 990 | 966 | 653 | 313 | 252 | 4.1 | - | NIL | 0.5 |  |  | 138
2023-12-21 | 6.88 | 61 |  | 0.8 | 1407 | 943 | 975 | 644 | 331 | 259 | 4 | - | NIL | 0.5 |  |  | 140
2023-12-22 | 7.39 | 65 |  | 0.8 | 1658 | 1111 | 1017 | 658 | 359 | 274 | 3.8 | - | NIL | 0.5 |  |  | 132
2023-12-23 | 7.89 | 61 |  | NIL | 1697 | 1018 | 1040 | 630 | 410 | 311 | 4.6 | - | NIL | 0.5 |  |  | 138
2023-12-25 | 8.64 | 98 |  | NIL | 1422 | 953 | 865 | 524 | 341 | 289 | 4.2 | - | NIL | 0.5 |  |  | 135
2023-12-26 | 7.9 | 78 |  | NIL | 1413 | 947 | 851 | 501 | 350 | 311 | 4.3 | - | NIL | 0.5 |  |  | 141
2023-12-27 | 7.54 | 62 |  | NIL | 1623 | 1088 | 925 | 469 | 456 | 274 | 2 | - | NIL | 0.5 |  |  | 138
2023-12-28 | 7.56 | 48 |  | NIL | 1618 | 1083 | 911 | 483 | 428 | 296 | 1.6 | - | NIL | 0.5 |  |  | 135
2023-12-29 | 7.41 | 42 |  | 1 | 1440 | 965 | 1012 | 621 | 391 | 311 | 1.5 |  | NIL | 0.5 |  |  | 142
2023-12-30 | 7.9 | 35 |  | NIL | 1461 | 979 | 994 | 543 | 451 | 326 | 1.7 |  | NIL | 0.5 |  |  | 121
01.01.24 | 7.16 | 26 |  | NIL | 1090 | 730 | 998 | 575 | 423 | 318 | 1.7 | - | NIL | 0.5 |  |  | 127
02.01.24 | 7.12 | 25 |  | NIL | 1072 | 712 | 980 | 561 | 419 | 281 | 2.2 | - | NIL | 0.5 |  |  | 133
03.01.24 | 7.7 | 31 |  | NIL | 939 | 629 | 989 | 578 | 411 | 296 | 1.9 | - | NIL | 0.5 |  |  | 124
04.01.24 | 7.7 | 42 |  | NIL | 920 | 617 | 998 | 561 | 437 | 311 | 2 | - | NIL | 0.5 |  |  | 120
2024-01-05 | 7.13 | 41 |  | NIL | 831 | 557 | 994 | 529 | 465 | 274 | 1.7 | - | NIL | 0.5 |  |  | 123
2024-01-06 | 7.05 | 41 |  | 0.8 | 761 | 510 | 1012 | 557 | 455 | 296 | 1.9 | - | NIL | 0.5 |  |  | 116
2024-01-08 | 7.41 |  |  | NIL | 671 | 450 | 322 | 143 | 179 | 59 | 2.1 | - | NIL | 0.5 |  |  | 60
2024-01-09 | 7.4 | 46 |  | NIL | 771 | 517 | 331 | 147 | 184 | 59 | 2 | - | NIL | 0.5 |  |  | 66
2024-01-10 | 7.12 | 47 |  | NIL | 731 | 490 | 327 | 161 | 166 | 67 | 4.3 | - | NIL | 0.5 |  |  | 59
2024-01-11 | 7.2 | 51 |  | NIL | 833 | 558 | 331 | 193 | 138 | 67 | 4.2 | - | NIL | 0.5 |  |  | 60
12.01.24 | 7.1 | 46 |  | NIL | 867 | 581 | 363 | 207 | 156 | 59 | 3.5 | - | NIL | 0.5 |  |  | 48
2024-01-16 | 7.59 | 66 |  | NIL | 1163 | 779 | 391 | 193 | 198 | 37 | 3.3 | - | NIL | 0.5 |  |  | 46
2024-01-17 | 7.08 | 66 |  | NIL | 1316 | 882 | 352 | 182 | 170 | 37 | 3.5 | - | NIL | 0.5 |  |  | 51
2024-01-18 | 7.05 | 76 |  | NIL | 1370 | 918 | 356 | 187 | 169 | 37 | 3.8 | - | NIL | 0.5 |  |  | 55
2024-01-19 | 8.65 | 48 |  | NIL | 1448 | 970 | 432 | 199 | 233 | 45 | 3.5 | - | NIL | 0.5 |  |  | 43
2024-01-20 | 7.15 | 51 |  | NIL | 1466 | 982 | 475 | 212 | 263 | 37 | 3.1 | - | NIL | 0.5 |  |  | 47
2024-01-22 | 7.37 | 37 |  | NIL | 1624 | 1088 | 534 | 276 | 258 | 215 | 3.5 | - | NIL | 0.5 |  |  | 49
2024-01-23 | 7.69 | 34 |  | NIL | 1671 | 1120 | 780 | 428 | 352 | 185 |  | - | NIL | 0.5 |  |  | 62
2024-01-29 | 7.32 | 34 |  | NIL | 2447 | 1640 | 844 | 449 | 395 | 281 | 4.1 | - | NIL | 0.5 |  |  | 84
2024-01-30 | 7.11 | 51 |  | NIL | 2525 | 1692 | 852 | 454 | 398 | 281 | 3.9 | - | NIL | 0.5 |  |  | 76
2024-01-31 | 7.29 | 53 |  | NIL | 2664 | 1785 | 845 | 449 | 396 | 259 | 4.2 |  | NIL | 0.5 |  |  | 73
2024-02-01 | 7.05 | 27 |  | NIL | 2461 | 1649 | 823 | 443 | 380 | 274 | 4.1 | - | NIL | 0.5 |  |  | 70
2024-02-02 | 7.61 | 20 |  | NIL | 2483 | 1664 | 793 | 407 | 386 | 259 | 3.6 | - | NIL | 0.5 |  |  | 63
2024-02-03 | 7.5 | 13 |  | NIL | 2263 | 1516 | 814 | 420 | 394 | 252 | 3.2 | - | NIL | 0.5 |  |  | 62
2024-02-05 | 7.35 | 12 |  | NIL | 2382 | 1596 | 852 | 437 | 415 | 215 | 2.9 | - | NIL | 0.5 |  |  | 66
2024-02-06 | 7.1 | 37 |  | NIL | 2120 | 1421 | 810 | 424 | 386 | 237 | 3.1 | - | NIL | 0.5 |  |  | 69
2024-02-07 | 7.55 | 15 |  | NIL | 2261 | 1515 | 831 | 445 | 386 | 259 | 2.8 | - | NIL | 0.5 |  |  | 61
2024-02-08 | 7.77 | 39 |  | 0.5 | 2071 | 1388 | 750 | 428 | 322 | 252 | 2.5 | - | NIL | 0.5 |  |  | 69
2024-02-09 | 7.51 | 53 |  | 0.5 | 1968 | 1319 | 776 | 437 | 339 | 266 | 2.8 | - | NIL | 0.5 |  |  | 72
2024-02-10 | 7.29 | 39 |  | 0.5 | 2022 | 1355 | 767 | 420 | 347 | 244 | 3.1 | - | NIL | 0.5 |  |  | 66
2024-02-12 | 7.66 | 30 |  | NIL | 1673 | 1121 | 636 | 301 | 335 | 244 | 3.4 | - | NIL | 0.5 |  |  | 72
2024-02-13 | 7.19 | 28 |  | NIL | 1611 | 1080 | 644 | 310 | 334 | 259 | 3.1 | - | NIL | 0.5 |  |  | 68
2024-02-14 | 7.27 | 25 |  | NIL | 2094 | 1403 | 704 | 301 | 403 | 244 | 2.8 | - | NIL | 0.5 |  |  | 72
2024-02-15 | 7.55 | 21 |  | NIL | 2008 | 1346 | 691 | 288 | 403 | 229 | 3.2 | - | NIL | 0.5 |  |  | 71
2024-02-16 | 7.84 | 15 |  | NIL | 2034 | 1363 | 742 | 267 | 475 | 215 | 2.8 | - | NIL | 0.5 |  |  | 68
2024-02-20 | 7.29 | 14 |  | NIL | 2619 | 1755 | 784 | 479 | 305 | 244 | 3.1 | - | NIL | 0.5 |  |  | 56
2024-02-21 | 7.41 | 24 |  | NIL | 2612 | 1750 | 810 | 471 | 339 | 222 | 3.3 | - | NIL | 0.5 |  |  | 66
2024-02-22 | 7.5 | 24 |  | NIL | 2544 | 1705 | 797 | 458 | 339 | 237 | 3.1 | - | NIL | 0.5 |  |  | 61
2024-02-23 | 7.27 | 17 |  | NIL | 2878 | 1928 | 818 | 488 | 330 | 259 | 2.8 | - | NIL | 0.5 |  |  | 55
2024-02-26 | 7.76 | 48 |  | NIL | 2478 | 1660 | 907 | 522 | 385 | 281 | 3.9 | - | NIL | 0.5 |  |  | 68
2024-02-27 | 7.34 | 39 |  | NIL | 2508 | 1681 | 895 | 509 | 386 | 224 | 4.1 | - | NIL | 0.5 |  |  | 65
2024-02-28 | 7.4 | 25 |  | NIL | 2397 | 1606 | 903 | 517 | 386 | 259 | 3.9 | - | NIL | 0.5 |  |  | 63
2024-02-29 | 7.42 | 26 |  | NIL | 2335 | 1565 | 912 | 522 | 390 | 281 | 4.1 | - | NIL | 0.5 |  |  | 69
01.03.24 | 7.12 | 51 |  | 0.8 | 2582 | 1730 | 941 | 572 | 369 | 238 | 3.8 | - | NIL | 0.6 |  |  | 59
02.03.24 | 7.66 | 40 |  | NIL | 2686 | 1800 | 984 | 530 | 454 | 209 | 3.1 | - | NIL | 0.7 |  |  | 55
04.03.24 | 7.7 | 19 |  | NIL | 2805 | 1880 | 958 | 530 | 428 | 252 | 3.3 | - | NIL | 0.6 |  |  | 51
05.03.24 | 7.76 | 30 |  | NIL | 2850 | 1910 | 984 | 543 | 441 | 238 | 3.5 | - | NIL | 0.6 |  |  | 55
06.03.24 | 7.51 | 41 |  | NIL | 2753 | 1845 | 971 | 522 | 449 | 223 | 2.9 | - | NIL | 0.6 |  |  | 49
2024-03-07 | 7.46 | 38 |  | NIL | 3090 | 2070 | 984 | 526 | 458 | 216 | 2.5 | - | NIL | 0.6 |  |  | 51
09.03.24 | 7.6 | 29 |  | NIL | 3448 | 2310 | 1128 | 585 | 543 | 259 | 3.2 | - | NIL | 0.5 |  |  | 53
11.03.24 | 7.12 | 25 |  | NIL | 4641 | 3110 | 1433 | 789 | 644 | 303 | 3.8 | - | NIL | 0.5 |  |  | 67
2024-03-12 | 7.9 | 28 |  | NIL | 3403 | 2280 | 1412 | 776 | 636 | 274 | 3.6 | - | NIL | 0.6 |  |  | 61
2024-03-13 | 7.02 | 68 |  | 0.7 | 3850 | 2580 | 1389 | 744 | 645 | 288 | 3.7 | - | NIL | 0.5 |  |  | 57
2024-03-14 | 7.36 | 74 |  | 0.4 | 3402 | 2280 | 1364 | 724 | 640 | 274 | 3.5 | - | NIL | 0.5 |  |  | 62
15.03.24 | 7.29 | 55 |  | NIL | 2866 | 1920 | 1314 | 724 | 590 | 245 | 3.2 | - | NIL | 0.5 |  |  | 64
2024-03-18 | 7.21 | 27 |  | NIL | 2701 | 1810 | 1190 | 619 | 571 | 259 | 3.1 | - | NIL | 0.5 |  |  | 61
2024-03-19 | 8 | 20 |  | NIL | 2611 | 1750 | 1135 | 606 | 529 | 223 | 3.9 | - | NIL | 0.4 |  |  | 63
20.03.24 | 7.28 | 42 |  | NIL | 2629 | 1762 | 1140 | 597 | 543 | 238 | 3.6 | - | NIL | 0.5 |  |  | 76
2024-03-21 | 7.1 | 53 |  | NIL | 2912 | 1951 | 1126 | 593 | 533 | 231 | 3.5 | - | NIL | 0.5 |  |  | 75
2024-03-22 | 7.32 | 44 |  | 0.2 | 2701 | 1810 | 1154 | 597 | 557 | 259 | 3.3 | - | NIL | 0.6 |  |  | 69
2024-03-23 | 7.52 | 21 |  | NIL | 2425 | 1625 | 1149 | 593 | 556 | 245 | 3.2 | - | NIL | 0.5 |  |  | 74
2024-03-26 | 7.94 | 19 |  | NIL | 2552 | 1710 | 1072 | 588 | 484 | 225 | 3.1 | - | NIL | 0.5 |  |  | 73
2024-03-27 | 7.2 | 94 |  | 0.9 | 2733 | 1831 | 1058 | 570 | 488 | 233 | 3.5 | - | NIL | 0.5 |  |  | 69
2024-03-28 | 7.27 | 86 |  | 0.7 | 2435 | 1632 | 1053 | 565 | 488 | 218 | 3.3 | - | NIL | 0.5 |  |  | 65
2024-03-29 | 7.67 | 90 |  | NIL | 2618 | 1754 | 1076 | 602 | 474 | 233 | 3.5 | - | NIL | 0.6 |  |  | 74
2024-03-30 | 7.3 | 73 |  | NIL | 2670 | 1789 | 1067 | 625 | 442 | 189 | 3.2 | - | NIL | 0.6 |  |  | 84
2024-04-02 | 7.41 | 34 |  | NIL | 2671 | 1790 | 1195 | 620 | 575 | 233 | 3.5 | - | NIL | 0.5 |  |  | 79
2024-04-03 | 7.22 | 31 |  | NIL | 2794 | 1872 | 1158 | 606 | 552 | 218 | 3.4 | - | NIL | 0.5 |  |  | 82
2024-04-04 | 7.36 | 30 |  | NIL | 2541 | 1703 | 1080 | 551 | 529 | 218 | 3.2 | - | NIL | 0.5 |  |  | 89
2024-04-05 | 6 | 49 |  | 1 | 2671 | 1790 | 1071 | 547 | 524 | 225 | 3.1 | - | NIL | 0.5 |  |  | 78
2024-04-08 | 7.29 | 56 |  | NIL | 3402 | 2280 | 1030 | 600 | 430 | 254 | 3.3 | - | NIL | 0.5 |  |  | 84
2024-04-09 | 7.28 | 59 |  | NIL | 3089 | 2070 | 1021 | 591 | 430 | 247 | 3.4 | - | NIL | 0.5 |  |  | 51
2024-04-10 | 7.26 | 45 |  | NIL | 3348 | 2310 | 1012 | 542 | 470 | 254 | 3.7 | - | NIL | 0.5 |  |  | 53
2024-04-11 | 7.88 | 41 |  | NIL | 3552 | 2380 | 1021 | 538 | 483 | 262 | 3.5 | - | NIL | 0.6 |  |  | 54
2024-04-12 | 7.1 | 44 |  | NIL | 3641 | 2440 | 1017 | 573 | 444 | 254 | 3.7 | - | NIL | 0.5 |  |  | 62
2024-04-16 | 7.2 | 40 |  | NIL | 3343 | 2240 | 1008 | 551 | 457 | 233 | 3.5 | - | NIL | 0.5 |  |  | 65
2024-04-17 | 7.1 | 32 |  | NIL | 3611 | 2420 | 1030 | 569 | 461 | 254 | 3.6 | - | NIL | 0.5 |  |  | 71
2024-04-18 | 7.6 | 58 |  | NIL | 3611 | 2420 | 1035 | 560 | 475 | 247 | 3.5 | - | NIL | 0.5 |  |  | 76
2024-04-19 | 7.1 | 7 |  | NIL | 3104 | 2080 | 1026 | 556 | 470 | 254 | 3.6 | - | NIL | 0.5 |  |  | 79
2024-04-22 | 7.21 | 34 |  | NIL | 2682 | 1797 | 1021 | 538 | 483 | 254 | 3.6 | - | NIL | 0.5 |  |  | 76
2024-04-23 | 7.02 | 22 |  | 0.4 | 2608 | 1748 | 968 | 564 | 404 | 480 | 4 | - | NIL | 0.5 |  |  | 59
2024-04-24 | 7.12 | 59 |  | 0.5 | 2296 | 1538 | 963 | 556 | 407 | 247 | 4.1 | - | NIL | 0.5 |  |  | 74
2024-04-25 | 7.49 | 47 |  | 0.5 | 1897 | 1271 | 954 | 551 | 403 | 254 | 4 | - | NIL | 0.5 |  |  | 72
2024-04-26 | 7.8 | 67 |  | 0.7 | 2641 | 1770 | 981 | 556 | 425 | 240 | 4.2 | - | NIL | 0.6 |  |  | 69
2024-04-29 | 7.25 | 89 |  | 0.5 | 1044 | 1122 | 815 | 358 | 457 | 233 | 4.2 | - | NIL | 0.5 |  |  | 73
2024-04-30 | 7.4 | 85 |  | 0.4 | 2180 | 1461 | 811 | 367 | 444 | 240 | 4.3 | - | NIL | 0.6 |  |  | 76
2024-05-01 | 7.29 | 114 |  | 0.8 | 1398 | 1272 | 833 | 385 | 448 | 233 | 4.4 | - | NIL | 0.5 |  |  | 72
2024-05-02 | 7.78 | 93 |  | 0.5 | 2168 | 1453 | 860 | 408 | 452 | 225 | 4.6 | - | NIL | 0.5 |  |  | 78
2024-05-03 | 7.33 | 93 |  | 0.9 | 2015 | 1350 | 900 | 457 | 443 | 240 | 4.3 | - | NIL | 0.5 |  |  | 81
2024-05-04 | 7.15 | 100 |  | 0.7 | 2045 | 1370 | 918 | 506 | 412 | 262 | 4.5 | - | NIL | 0.7 |  |  | 77
2024-05-06 | 7.45 | 72 |  | 0.3 | 2179 | 1460 | 887 | 457 | 430 | 247 | 4.2 | - | NIL | 0.3 |  |  | 83
2024-05-07 | 7.46 | 62 |  | Nil | 2086 | 1398 | 840 | 441 | 399 | 276 | 4.3 | - | NIL | 0.6 |  |  | 80
2024-05-08 | 7.5 | 63 |  | Nil | 1923 | 1329 | 857 | 554 | 303 | 257 | 4.2 | - | NIL | 0.6 |  |  | 75
2024-05-09 | 7.81 | 50 |  | 0.5 | 4204 | 2817 | 865 | 546 | 319 | 265 | 4.3 | - | NIL | 0.6 |  |  | 79
2024-05-10 | 7.76 | 78 |  | 0.2 | 2068 | 1398 | 861 | 550 | 311 | 257 | 4.2 | - | NIL | 0.2 |  |  | 78
2024-05-11 | 8 | 60 |  | 0.6 | 1703 | 1141 | 853 | 504 | 349 | 279 | 4.5 | - | NIL | 0.5 |  |  | 83
2024-05-13 | 8.07 | 62 |  | Nil | 1850 | 1240 | 924 | 550 | 374 | 309 | 4.6 | - | NIL | 0.5 |  |  | 74
2024-05-15 | 8.19 | 82 |  | Nil | 2093 | 1402 | 894 | 510 | 384 | 316 | 4.6 | - | NIL | 0.5 |  |  | 82
2024-05-16 | 8.6 | 74 |  | 0.2 | 2156 | 1445 | 914 | 526 | 388 | 309 | 4.5 | - | NIL | 0.5 |  |  | 78
2024-05-17 | 7.8 | 83 |  | 1 | 2267 | 1519 | 918 | 522 | 396 | 301 | 4.6 | - | NIL | 0.5 |  |  | 74
2024-05-18 | 7.33 | 104 |  | 0.6 | 2300 | 1541 | 922 | 530 | 392 | 294 | 4.1 | - | NIL | 0.5 |  |  | 78
2024-05-20 | 7.73 | 73 |  | 0.3 | 1868 | 1252 | 922 | 534 | 388 | 301 | 4.3 | - | NIL | 0.5 |  |  | 76
2024-05-21 | 7.4 | 63 |  | 0.3 | 1895 | 1270 | 961 | 557 | 404 | 316 | 4.5 | - | NIL | 0.5 |  |  | 72
2024-05-23 | 7.42 | 42 |  | 0.5 | 1847 | 1238 | 978 | 566 | 412 | 316 | 5.1 | - | NIL | 0.4 |  |  | 81
2024-05-24 | 7.12 | 51 |  | 0.5 | 1964 | 1316 | 969 | 562 | 407 | 309 | 4.7 | - | NIL | 0.5 |  |  | 79
2024-05-25 | 7.48 | 53 |  | 0.6 | 1901 | 1274 | 924 | 532 | 392 | 301 | 4.5 | - | NIL | 0.5 |  |  | 80
2024-05-27 | 7.44 | 54 |  | 0.5 | 2005 | 1344 | 761 | 428 | 333 | 309 | 4.2 | - | NIL | 0.5 |  |  | 76
2024-05-28 | 7.06 | 53 |  | 0.7 | 2333 | 1563 | 770 | 433 | 337 | 316 | 4.3 | - | NIL | 0.5 |  |  | 75
2024-05-29 | 7.44 | 53 |  | 0.1 | 1992 | 1335 | 745 | 453 | 292 | 316 | 4.6 | - | NIL | 0.5 |  |  | 82
2024-05-30 | 7.84 | 66 |  | 0.6 | 2156 | 1445 | 799 | 478 | 321 | 309 | - |  | NIL | 0.4 |  |  | 85
2024-05-31 | 7.1 | 67 |  | 0.7 | 1868 | 1252 | 811 | 495 | 316 | 316 | 4.3 | - | NIL | 0.4 |  |  | 82
2024-06-01 | 7.34 | 65 |  | 0.8 | 1597 | 1070 | 982 | 549 | 433 | 309 | 2.6 | - | NIL | 0.5 |  |  | 76
2024-06-03 | 7.82 | 49 |  | 1 | 1493 | 1027 | 774 | 428 | 346 | 272 | 2.5 | - | NIL | 0.5 |  |  | 71
2024-06-04 | 7.4 | 38 |  | 0.6 | 1559 | 1045 | 786 | 449 | 337 | 279 | 2.7 | - | NIL | 0.5 |  |  | 68
2024-06-05 | 8.1 | 33 |  | 0.5 | 2037 | 1365 | 603 | 366 | 237 | 254 | 2.6 | - | NIL | 0.5 |  |  | 71
2024-06-07 | 7.89 | 46 |  | 0.5 | 1934 | 1296 | 861 | 479 | 382 | 282 | 2.1 | - | NIL | 0.6 |  |  | 64
2024-06-08 | 7.43 | 28 |  | 0.2 | 1808 | 1212 | 729 | 382 | 347 | 257 | 2.6 | - | NIL | 0.5 |  |  | 79
2024-06-10 | 7.45 | 28 |  | NIL | 1792 | 1201 | 742 | 386 | 356 | 282 | 2.8 | - | NIL | 0.4 |  |  | 85
2024-06-11 | 7.58 | 19 |  | NIL | 2029 | 1360 | 755 | 399 | 356 | 287 | 2.5 | - | NIL | 0.4 |  |  | 82
2024-06-12 | 7.25 | 32 |  | 0.6 | 2101 | 1408 | 772 | 416 | 356 | 272 | 2.6 | - | NIL | 0.4 |  |  | 78
2024-06-13 | 6.22 | 47 |  | 0.7 | 2641 | 1770 | 827 | 441 | 386 | 287 | 2.5 | - | NIL | 0.5 |  |  | 81
2024-06-14 | 7.71 | 41 |  | NIL | 2612 | 1750 | 866 | 454 | 412 | 279 | 2.2 | - | NIL | 0.4 |  |  | 83
2024-06-15 | 6.7 | 50 |  | NIL | 2799 | 1875 | 926 | 561 | 365 | 309 | 2.6 | - | NIL | 0.5 |  |  | 78
2024-06-17 | 7.6 | 40 |  | NIL | 3880 | 2600 | 1031 | 586 | 445 | 316 | 2.7 | - | NIL | 0.5 |  |  | 77
2024-06-19 | 7.72 | 40 |  | NIL | 2753 | 1945 | 1072 | 606 | 466 | 323 | 2.6 | - | NIL | 0.5 |  |  | 82
2024-06-20 | 7.85 | 42 |  | NIL | 2254 | 1510 | 1033 | 597 | 436 | 309 | 2.8 | - | NIL | 0.5 |  |  | 79
2024-06-21 | 7.5 | 54 |  | NIL | 2447 | 1640 | 1042 | 384 | 658 | 301 | 2.9 | - | NIL | 0.5 |  |  | 76
2024-06-22 | 7.52 | 55 |  | NIL | 4074 | 2730 | 1046 | 589 | 457 | 294 | 2.8 | - | NIL | 0.5 |  |  | 75
2024-06-24 | 7.49 | 57 |  | 0.2 | 2314 | 1551 | 1033 | 593 | 440 | 309 | 2.7 | - | NIL | 0.5 |  |  | 76
2024-06-25 | 7.34 | 105 |  | NIL | 2958 | 1982 | 1061 | 613 | 448 | 320 | 2.5 | - | NIL | 0.5 |  |  | 72
26.06.24 | 7.88 | 263 |  | NIL | 2589 | 1735 | 1070 | 599 | 471 | 298 | 2.5 | - | NIL | 0.5 |  |  | 73
2024-06-27 | 7.88 | 75 |  | NIL | 1989 | 1333 | 1043 | 577 | 466 | 284 | 2.3 | - | NIL | 0.5 |  |  | 75
2024-06-28 | 7.69 | 39 |  | NIL | 2153 | 1443 | 1057 | 577 | 480 | 291 | 2.1 | - | NIL | 0.5 |  |  | 72
2024-06-29 | 7.17 | 37 |  | NIL | 2291 | 1535 | 1074 | 591 | 483 | 298 | 2.3 | - | NIL | 0.5 |  |  | 69
2024-07-01 | 7.39 | 16 |  | NIL | 2704 | 1812 | 819 | 407 | 412 | 284 | 2.5 | - | NIL | 0.4 |  |  | 83
2024-07-02 | 7.35 | 31 |  | NIL | 3328 | 2230 | 821 | 401 | 420 | 270 | 2.3 | - | NIL | 0.5 |  |  | 81
2024-07-03 | 7.65 | 22 |  | NIL | 2702 | 1811 | 859 | 414 | 445 | 277 | 2.4 | - | NIL | 0.5 |  |  | 78
2024-07-04 | 8.11 | 32 |  | NIL | 1902 | 1275 | 784 | 401 | 383 | 249 | 2.5 | - | NIL | 0.4 |  |  | 75
2024-07-05 | 7.94 | 16 |  | NIL | 2931 | 1964 | 807 | 420 | 387 | 256 | 2.4 | - | NIL | 0.5 |  |  | 76
2024-07-06 | 7.16 | 35 |  | 0.7 | 2955 | 1980 | 864 | 406 | 458 | 234 | 2.6 | - | NIL | 0.5 |  |  | 84
2024-07-08 | 7.49 | 30 |  | NIL | 2517 | 1687 | 800 | 381 | 419 | 241 | 2.7 | - | NIL | 0.5 |  |  | 78
2024-07-09 | 7.56 | 33 |  | NIL |  | 1641 | 809 | 390 | 419 | 256 | 2.5 | - | NIL | 0.5 |  |  | 79
2024-07-10 | 7.24 | 32 |  | NIL | 3194 | 2140 | 847 | 419 | 428 | 249 | 2.7 | - | NIL | 0.5 |  |  | 81
2024-07-11 | 7.64 | 49 |  | 0.2 | 2955 | 1980 | 919 | 395 | 524 | 241 | 2.6 | - | NIL | 0.5 |  |  | 77
2024-07-12 | 7.3 | 43 |  | 0.6 | 2626 | 1760 | 995 | 560 | 435 | 292 | 2.6 | - | NIL | 0.5 |  |  | 83
2024-07-13 | 7.36 | 40 |  | 0.5 | 2325 | 1558 | 925 | 525 | 400 | 275 | 2.5 | - | NIL | 0.5 |  |  | 78
2024-07-15 | 7.08 | 54 |  | 0.6 | 2640 | 1769 | 960 | 560 | 400 | 284 | 2.3 | - | NIL | 0.5 |  |  | 82
2024-07-16 | 8.08 | 62 |  | 0.5 | 2207 | 1479 | 1010 | 575 | 435 | 259 | 2.5 | - | NIL | 0.5 |  |  | 80
2024-07-17 | 7.99 | 59 |  | 0.5 | 2253 | 1510 | 990 | 495 | 495 | 267 | 2.5 | - | NIL | 0.5 |  |  | 79
2024-07-18 | 7.1 | 57 |  | 0.9 | 2785 | 1866 | 1000 | 490 | 510 | 284 | 2.4 | - | NIL | 0.5 |  |  | 80
2024-07-19 | 8.29 | 80 |  | NIL | 2397 | 1606 | 995 | 495 | 500 | 275 | 2.3 | - | NIL | 0.5 |  |  | 80
2024-07-20 | 7.47 | 47 |  | NIL | 2612 | 1750 | 945 | 482 | 463 | 292 | 1.9 | - | NIL | 0.6 |  |  | 82
2024-07-22 | 7.78 | 58 |  | NIL | 1626 | 1090 | 964 | 473 | 491 | 267 | 1.9 | - | NIL | 0.5 |  |  | 79
2024-07-23 | 7.61 | 36 |  | NIL | 1743 | 1168 | 978 | 482 | 496 | 284 | 2 | - | NIL | 0.5 |  |  | 80
2024-07-24 | 6.86 | 38 |  | NIL | 1628 | 1091 | 927 | 459 | 468 | 275 | 2.2 | - | NIL | 0.5 |  |  | 74
2024-07-25 | 7.19 | 27 |  | NIL | 1405 | 942 | 913 | 449 | 464 | 259 | 2.1 | - | NIL | 0.5 |  |  | 76
2024-07-26 | 7.15 | 25 |  | NIL | 1346 | 902 | 922 | 445 | 477 | 267 | 2.2 | - | NIL | 0.5 |  |  | 75
2024-07-27 | 7.77 | 24 |  | NIL | 1580 | 1058 | 917 | 442 | 475 | 263 | 2.2 | - | NIL | - |  |  | 74
2024-07-29 | 7.15 | 44 |  | 0.6 | 1573 | 1054 | 772 | 417 | 355 | 267 | 2.2 | - | NIL | 0.5 |  |  | 75
2024-07-30 | 7.11 | 24 |  | NIL | 1582 | 1060 | 786 | 426 | 360 | 292 | 2.1 | - | NIL | 0.5 |  |  | 75
2024-07-31 | 7.22 | 20 |  | NIL | 1761 | 1180 | 824 | 445 | 379 | 284 | 2.2 | - | NIL | 0.5 |  |  | 77
01.09.25 | 8.45 | 34 | 22 | Nil | 1865 | 1249 | 810 | 502 | 308 | 355 | 7.5 | 122 | 2 | 0.3 |  |  | -
03.09.25 | 8.2 | - | 26 | Nil | 2179 | 1460 | 963 | 609 | 354 | 379 | 7 | 124 | Nil | 0.4 |  |  | 80
04.09.25 | 8.14 | - | 30 | 0.8 | 2413 | 1617 | 896 | 600 | 296 | 336 | 6.9 | 134 | Nil | 0.5 |  |  | 78
05.09.25 | 7.8 | - | 27 | Nil | 1895 | 1270 | 778 | 563 | 215 | 270 | 6.8 | 118 | Nil | 0.4 |  |  | 72
06.09.25 | 8.35 | - | 25 | Nil | 1567 | 1050 | 721 | 553 | 168 | 250 | 6.8 | 126 | Nil | 0.4 |  |  | 70
07.09.25 | 8.3 | - | 20 | Nil | 1671 | 1120 | 618 | 367 | 251 | 243 | 7.2 | 122 | Nil | 0.3 |  |  | 72
08.09.25 | 8.55 | - | 19 | 0.2 | 1627 | 1090 | 624 | 401 | 223 | 243 | 6.9 | 125 | 2 | 0.2 |  |  | 70
09.09.25 | 8.1 | - | 28 | 1 | 1654 | 1108 | 638 | 369 | 269 | 264 | 7 | 96 | Nil | 0.3 |  |  | 80
10.09.25 | 8.2 | - | 19 | 0.1 | 1611 | 1080 | 622 | 378 | 244 | 250 | 6.5 | 113 | Nil | 0.4 |  |  | 70
11.09.25 | 8.09 | - | 20 | 0.1 | 1572 | 1053 | 612 | 359 | 253 | 265 | 6.3 | 110 | Nil | 0.4 |  |  | 79
12.09.25 | 8.08 | - | 19 | 0.1 | 1761 | 1180 | 606 | 324 | 282 | 224 | 6.8 | 110 | Nil | 0.4 |  |  | 80
13.09.25 | 8.45 | - | 15 | 0.2 | 1776 | 1190 | 600 | 330 | 270 | 190 | 7 | 117 | 1 | 0.6 |  |  | 76
14.09.25 | 8.35 | - | 17 | Nil | 1835 | 1230 | 623 | 340 | 283 | 201 | 6.9 | 110 | Nil | 0.6 |  |  | 72
15.09.25 | 8.32 | - | 19 | 0.1 | 1761 | 1180 | 582 | 312 | 270 | 208 | 6.5 | 120 | Nil | 0.6 |  |  | 75
16.09.25 | 8.1 | - | 22 | 1 | 1815 | 1216 | 821 | 440 | 381 | 289 | 7.2 | 123 | Nil | 0.7 |  |  | 105
17.09.25 | 8.26 | - | 25 | Nil | 2044 | 1370 | 860 | 500 | 360 | 295 | 7 | 112 | Nil | 0.6 |  |  | 92
18.09.25 | 8.1 | - | 23 | 0.1 | 2223 | 1490 | 838 | 480 | 358 | 280 | 6.8 | 120 | Nil | 0.6 |  |  | 112
19.09.25 | 8.49 | - | 23 | 0.1 | 2164 | 1450 | 906 | 497 | 409 | 290 | 7.2 | 129 | 2 | 0.7 |  |  | 120
20.09.25 | 8.78 | - | 13 | 0.1 | 2035 | 1364 | 896 | 515 | 381 | 282 | 7 | 138 | 3 | 0.7 |  |  | 115
21.09.25 | 8.66 | - | 19 | 0.1 | 1985 | 1330 | 870 | 500 | 370 | 284 | 7.1 | 133 | 2 | 0.7 |  |  | 118
22.09.25 | 8.1 | - | 16 | 0.1 | 1821 | 1220 | 875 | 492 | 383 | 280 | 6.9 | 127 | Nil | 0.6 |  |  | 109
23.09.25 | 8.63 | - | 13 | 0.1 | 1725 | 1158 | 792 | 256 | 536 | 274 | 7.3 | 135 | 2 | 0.5 |  |  | 124
24.09.25 | 8.7 | - | 13 | 0.1 | 2078 | 1392 | 882 | 470 | 412 | 261 | 6.8 | 129 | 3 | 0.6 |  |  | 134
25.09.25 | 8.29 | - | 14 | 0.1 | 2030 | 1360 | 875 | 468 | 407 | 260 | 6.9 | 120 | Nil | 0.6 |  |  | 127
26.09.25 | 8.35 | - | 19 | 1 | 2082 | 1395 | 931 | 502 | 429 | 289 | 7 | 126 | Nil | 0.8 |  |  | 130
27.09.25 | 8.54 | - | 23 | 0.1 | 2228 | 1493 | 953 | 508 | 445 | 285 | 7.2 | 134 | 2 | 0.7 |  |  | 127
28.09.25 | 8.4 | - | 23 | 0.1 | 1985 | 1330 | 931 | 493 | 438 | 268 | 7.1 | 122 | 2 | 0.6 |  |  | 119
29.09.25 | 8.12 | - | 18 | 0.1 | 1866 | 1250 | 891 | 551 | 340 | 106 | 7.2 | 106 | Nil | 0.7 |  |  | 115
30.09.25 | 8.4 | - | 20 | 0.1 | 1895 | 1270 | 912 | 560 | 352 | 261 | 7 | 120 | 1 | 0.5 |  |  | 119
01.10.25 | 8.3 | - | 18 | 0.1 | 1716 | 1150 | 850 | 542 | 308 | 260 | 6.5 | 120 | NIL | 0.6 |  |  | 130
02.10.25 | 8.5 | - | 13 | 0.1 | 2164 | 1450 | 784 | 538 | 246 | 281 | 6.2 | 123 | 2 | 0.5 |  |  | 122
03.10.25 | 8.42 | - | 14 | 0.1 | 1970 | 1320 | 779 | 476 | 303 | 231 | 7 | 119 | 2 | 0.6 |  |  | 160
04.10.25 | 8.1 | - | 15 | 0.1 | 1768 | 1185 | 770 | 472 | 298 | 240 | 6.7 | 112 | NIL | 0.5 |  |  | 152
06.10.25 | 8.25 | - | 16 | 0.1 | 1671 | 1120 | 824 | 456 | 368 | 209 | 7 | 110 | NIL | 0.5 |  |  | 150
07.10.25 | 8.32 | - | 12 | 0.1 | 2130 | 1461 | 779 | 439 | 340 | 295 | 7 | 118 | NIL | 0.5 |  |  | 169
08.10.25 | 8.5 | - | 12 | 0.1 | 2308 | 1547 | 786 | 490 | 296 | 237 | 6.8 | 121 | 3 | 0.6 |  |  | 150
09.10.25 | 8.45 | - | 15 | 0.1 | 2223 | 1490 | 760 | 482 | 278 | 227 | 6.5 | 130 | 2 | 0.5 |  |  | 136
10.10.25 | 8.5 | - | 15 | 0.4 | 1776 | 1190 | 775 | 435 | 340 | 224 | 6.3 | 138 | 3 | 0.4 |  |  | 131
11.10.25 | 8.9 | - | 12 | 0.1 | 1726 | 1157 | 747 | 458 | 289 | 250 | 6.5 | 147 | 3 | 0.5 |  |  | 126
13.10.25 | 8.6 | - | 12 | Nil | 2208 | 1480 | 840 | 461 | 379 | 242 | 6.7 | 129 | 3 | 0.5 |  |  | 163
14.10.25 | 8.48 | - | 14 | 0.1 | 2298 | 1540 | 835 | 439 | 396 | 248 | 6.4 | 133 | 2 | 0.6 |  |  | 158
15.10.25 | 8.6 | - | 15 | Nil | 2119 | 1420 | 798 | 462 | 336 | 252 | 6.1 | 132 | 2 | 0.6 |  |  | 121
16.10.25 | 8.7 | - | 10 | Nil | 2119 | 1420 | 780 | 440 | 340 | 248 | 6 | 138 | 3 | 0.6 |  |  | 130
17.10.25 | 8.7 | - | 11 | Nil | 2343 | 1570 | 770 | 420 | 350 | 247 | 6.1 | 132 | 3 | 0.6 |  |  | 127
18.10.25 | 8.71 | - | 11 | Nil | 2177 | 1459 | 751 | 440 | 311 | 234 | 6.3 | 140 | 3 | 0.5 |  |  | 137
21.10.25 | 8.6 | - | 13 | 0.1 | 2134 | 1430 | 793 | 458 | 335 | 220 | 5.9 | 130 | 2 | 0.5 |  |  | 125
24.10.25 | 8.82 | - | 35 | 1 | 3537 | 2370 | 1020 | 570 | 450 | 350 | 6 | 159 | 5 | 0.6 |  |  | 129
25.10.25 | 8.9 | - | 30 | 0.1 | 2723 | 1825 | 957 | 515 | 442 | 294 | 5.5 | 164 | 5 | 0.5 |  |  | 130
27.10.25 | 8.8 | - | 34 | 0.5 | 2954 | 1979 | 1008 | 564 | 444 | 316 | 5.9 | 122 | 2 | 0.7 |  |  | 139
28.10.25 | 8.6 | - | 23 | 0.8 | 2656 | 1780 | 920 | 550 | 370 | 320 | 6.2 | 134 | 3 | 0.7 |  |  | 140
29.10.25 | 8.4 | - | 19 | 0.5 | 2388 | 1600 | 880 | 563 | 317 | 300 | 7 | 132 | 2 | 0.7 |  |  | 131
30.10.25 | 8.32 | - | 19 | 0.5 | 2612 | 1750 | 893 | 560 | 333 | 322 | 6.9 | 138 | NIL | 0.7 |  |  | 142
31.10.25 | 8.1 | - | 23 | 0.5 | 2940 | 1970 | 904 | 528 | 376 | 340 | 6.2 | 125 | NIL | 0.7 |  |  | 148
MAX. | 8.3 | 28 |  | 0.8 | 3179 | 2130 | 1080 | 620 | 460 | 350 | 10.5 | 124 | 0 | 0.6 | 85 | 982 | 156
AVG. | 7.8793 | 19 |  | 0.27241 | 2193.0345 | 1468.4828 | 842 | 500.0345 | 341.9655 | 239.2414 | 6.7276 | 112.6897 | 0 | 0.44643 | 47.5172 | 878.6207 | 139.069
No. of < Spec | 0 | -- |  | 13 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 7 | 29 |  | 6 | -- | 1 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- |  | 44.8276 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | --
% > Specs. | 24.1379 | 100 |  | 20.6897 |  | 3.4483 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  | 0 | 0