## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | TSS | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | Max. 20 PPM | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2024-08-01 | 7.77 | 94 |  | NIL | 1714 | 1149 | 746 | 416 | 330 | 300 | 4.5 | - | NIL | 0.5 |  |  | 77
2024-08-02 | 8.32 | 81 |  | NIL | 1489 | 998 | 732 | 402 | 330 | 316 | 4.6 | - | NIL | 0.5 |  |  | 79
2024-08-03 | 8.33 | 84 |  | NIL | 1377 | 923 | 759 | 398 | 361 | 308 | 4.3 | - | NIL | 0.5 |  |  | 76
2024-08-05 | 8.13 | 61 |  | NIL | 1374 | 921 | 683 | 334 | 349 | 284 | 4.3 | - | NIL | 0.5 |  |  | 80
2024-08-06 | 8.39 | 59 |  | NIL | 1404 | 941 | 692 | 357 | 335 | 292 | 4.6 | - | NIL | 0.5 |  |  | 75
2024-08-07 | 7.94 | 62 |  | NIL | 1397 | 936 | 687 | 339 | 348 | 275 | 4.5 | - | NIL | 0.5 |  |  | 78
2024-08-08 | 8.43 | 64 |  | NIL | 1331 | 892 | 701 | 348 | 353 | 284 | 4.4 | - | NIL | 0.5 |  |  | 74
2024-08-09 | 7.74 | 53 |  | NIL | 1305 | 875 | 692 | 339 | 353 | 292 | 4.5 | - | NIL | 0.5 |  |  | 76
2024-08-10 | 8.1 | 48 |  | NIL | 1089 | 730 | 737 | 353 | 384 | 300 | 4.4 | - | NIL | 0.6 |  |  | 72
2024-08-12 | 8.4 | 50 |  | 0.2 | 1341 | 899 | 502 | 235 | 267 | 273 | 4.3 | - | NIL | 0.6 |  |  | 79
2024-08-13 | 6.5 | 78 |  | 1 | 1562 | 1047 | 524 | 244 | 280 | 268 | 4.5 | - | NIL | 0.6 |  |  | 72
2024-08-14 | 7.3 | 68 |  | 0.4 | 1541 | 1033 | 506 | 258 | 248 | 251 | 4.2 | - | NIL | 0.5 |  |  | 78
2024-08-16 | 7.32 | 33 |  | 0.6 | 1589 | 1065 | 699 | 354 | 345 | 251 | 4.2 | - | NIL | 0.5 |  |  | 76
2024-08-17 | 7.27 | 85 |  | 0.5 | 1573 | 1054 | 621 | 331 | 290 | 235 | 4.3 | - | NIL | 0.5 |  |  | 77
2024-08-20 | 7.4 | 70 |  | 1 | 1549 | 1038 | 708 | 327 | 381 | 259 | 4.4 | - | NIL | 0.5 |  |  | 96
2024-08-21 | 7.95 | 58 |  | NIL | 1405 | 942 | 713 | 331 | 382 | 267 | 4.5 | - | NIL | - |  |  | 95
2024-08-22 | 7.84 | 60 |  | 0.6 | 1404 | 941 | 704 | 327 | 377 | 251 | 4.3 | - | NIL | 0.5 |  |  | 90
2024-08-23 | 6.96 | 55 |  | 0.8 | 1400 | 938 | 695 | 350 | 345 | 286 | 4.6 | - | NIL | 0.5 |  |  | 96
2024-08-24 | 7 | 52 |  | 0.5 | 1450 | 972 | 810 | 409 | 401 | 292 | 4.4 | - | NIL | 0.6 |  |  | 85
2024-08-27 | 7.6 | 60 |  | NIL | 1223 | 820 | 460 | 278 | 182 | 211 | 4 | - | NIL | 0.5 |  |  | 78
2024-08-28 | 8.3 | 52 |  | NIL | 1077 | 722 | 699 | 299 | 400 | 251 | 4.3 | - | NIL | 0.5 |  |  | 86
2024-08-29 | 7.36 | 50 |  | 0.5 | 1120 | 751 | 727 | 285 | 442 | 243 | 4.2 | - | NIL | 0.5 |  |  | 81
2024-08-30 | 7.64 | 39 |  | NIL | 923 | 619 | 566 | 294 | 272 | 219 | 4.2 | - | NIL | 0.5 |  |  | 87
2024-08-31 | 7.86 | 52 |  | NIL | 1104 | 740 | 621 | 352 | 269 | 211 | 4.3 |  | NIL | 0.6 |  |  | 83
2024-09-02 | 7 | 18 |  | 0.8 | 1244 | 834 | 552 | 504 | 48 | 212 | 3.3 | - | NIL | 0.5 |  |  | 80
2024-09-03 | 7.53 | 41 |  | NIL | 1088 | 729 | 561 | 193 | 368 | 368 | 3.5 | - | NIL | - |  |  | 78
2024-09-04 | 7.72 | 21 |  | 0.1 | 1198 | 803 | 575 | 235 | 340 | 227 | 3.6 | - | NIL | 0.5 |  |  | 85
2024-09-05 | 7.48 | 31 |  | NIL | 1029 | 690 | 501 | 216 | 285 | 178 | 3.2 | - | NIL | 0.5 |  |  | 90
2024-09-06 | 5.68 | 34 |  | 0.4 | 1062 | 712 | 515 | 202 | 313 | 252 | 3.4 | - | NIL | 0.5 |  |  | 81
07.09.24 | 7.2 | 40 |  | NIL | 1476 | 989 | 529 | 207 | 322 | 236 | 3.3 | - | NIL | 0.5 |  |  | 80
09.09.24 | 7.84 | 31 |  | NIL | 1004 | 673 | 520 | 198 | 322 | 228 | 3.1 | - | NIL | 0.5 |  |  | 81
2024-09-10 | 7.05 | 47 |  | 0.8 | 1126 | 755 | 442 | 147 | 295 | 203 | 3.2 | - | NIL | 0.5 |  |  | 78
11.09.24 | 7.96 | 38 |  | NIL | 1123 | 752 | 437 | 143 | 294 | 211 | 3.3 | - | NIL | 0.5 |  |  | 82
12.09.24 | 7.55 | 35 |  | 0.6 | 1134 | 760 | 432 | 138 | 294 | 204 | 3.1 | - | NIL | 0.5 |  |  | 80
13.09.24 | 7.32 | 46 |  | 0.2 | 1149 | 770 | 419 | 152 | 267 | 196 | 3.2 | - | NIL | 0.5 |  |  | 79
2024-09-14 | 7.92 | 30 |  | NIL | 1221 | 818 | 423 | 156 | 267 | 282 | 3.3 | - | NIL | 0.4 |  |  | 83
16.09.24 | 7.02 | 43 |  | 0.6 | 1101 | 738 | 520 | 198 | 322 | 175 | 3.1 | - | NIL | 0.5 |  |  | 81
2024-09-17 | 7.79 | 43 |  | NIL | 1311 | 879 | 529 | 207 | 322 | 204 | 3.2 | - | NIL | 0.5 |  |  | 79
2024-09-18 | 7.4 | 47 |  | 0.6 | 1362 | 913 | 515 | 221 | 294 | 182 | 3.5 | - | NIL | 0.5 |  |  | 85
19.09.24 | 7.5 | 28 |  | 0.5 | 1412 | 946 | 557 | 206 | 351 | 196 | 3.4 | - | NIL | 0.5 |  |  | 81
2024-09-20 | 7.93 | 31 |  | 0.5 | 1552 | 1040 | 547 | 211 | 336 | 189 | 3.5 | - | NIL | 0.5 |  |  | 78
21.09.24 | 7.92 | 38 |  | NIL | 1464 | 981 | 534 | 190 | 344 | 203 | 3.4 | - | NIL | 0.5 |  |  | 76
23.09.24 | 7.82 | 23 |  | NIL | 1510 | 1016 | 529 | 241 | 288 | 203 | 3.2 | - | NIL | 0.5 |  |  | 76
24.09.24 | 7.47 | 20 |  | NIL | 1476 | 989 | 548 | 232 | 316 | 187 | 3.1 | - | NIL | 0.5 |  |  | 75
2024-09-25 | 8.45 | 35 |  | NIL | 1382 | 926 | 552 | 237 | 315 | 179 | 3.2 | - | NIL | 0.5 |  |  | 76
2024-09-26 | 7.84 | 32 |  | NIL | 1280 | 858 | 538 | 209 | 329 | 195 | 3.5 | - | NIL | 0.5 |  |  | 80
2024-09-27 | 8.11 | 46 |  | NIL | 1593 | 1067 | 510 | 212 | 298 | 179 | 3.2 | - | NIL | 0.5 |  |  | 78
2024-09-28 | 7.6 | 42 |  | NIL | 1556 | 1043 | 505 | 207 | 298 | 187 | 3.4 | - | NIL | 0.5 |  |  | 81
30.09.24 | 7.95 | 26 |  | NIL | 1349 | 904 | 501 | 199 | 302 | 187 | 3.2 | - | NIL | 0.5 |  |  | 79
2024-10-01 | 8.16 | 25 |  | NIL | 1280 | 858 | 710 | 406 | 304 | 189 | 3.9 | - | NIL | 0.6 |  |  | 85
2024-10-02 | 8.4 | 21 |  | NIL | 1243 | 833 | 691 | 394 | 297 | 160 | 4 | - | NIL | 0.6 |  |  | 81
03.10.24 | 8.25 | 19 |  | NIL | 1082 | 725 | 659 | 380 | 279 | 146 | 3.7 | - | NIL | 0.5 |  |  | 77
04.10.24 | 8.04 | 21 |  | NIL | 1343 | 900 | 843 | 385 | 458 | 175 | 3.8 | - | NIL | 0.5 |  |  | 79
2024-10-05 | 7.95 | 26 |  | NIL | 1323 | 887 | 668 | 380 | 288 | 160 | 3.9 | - | NIL | 0.5 |  |  | 82
07.10.24 | 8.73 | 19 |  | NIL | 1258 | 843 | 529 | 278 | 251 | 153 | 3.5 | - | NIL | 0.5 |  |  | 78
08.10.24 | 8.8 | 18 |  | NIL | 1220 | 818 | 547 | 280 | 267 | 167 | 3.8 | - | NIL | 0.5 |  |  | 82
09.10.24 | 8.82 | 22 |  | NIL | 1268 | 850 | 542 | 276 | 266 | 153 | 3.7 | - | NIL | 0.5 |  |  | 76
10.10.24 | 8.83 | 24 |  | NIL | 1326 | 889 | 565 | 280 | 285 | 146 | 3.5 | - | NIL | 0.5 |  |  | 80
11.10.24 | 8.49 | 25 |  | NIL | 1320 | 885 | 556 | 271 | 285 | 160 | 3.7 | - | NIL | 0.5 |  |  | 82
12.10.24 | 8.12 | 26 |  | NIL | 1365 | 915 | 551 | 285 | 266 | 146 | 3.6 | - | NIL | 0.5 |  |  | 78
14.10.24 | 7.48 | 25 |  | NIL | 1425 | 955 | 397 | 280 | 117 | 226 | 3.5 | - | NIL | 0.5 |  |  | 77
15.10.24 | 7.93 | 31 |  | NIL | 1396 | 935 | 601 | 278 | 323 | 175 | 3.2 | - | NIL | 0.5 |  |  | 79
16.10.24 | 8.23 | 22 |  | NIL | 1259 | 844 | 588 | 267 | 321 | 160 | 3.4 | - | NIL | 0.5 |  |  | 85
17.10.24 | 7.87 | 20 |  | 0.2 | 1250 | 838 | 579 | 262 | 317 | 153 | 3.3 | - | NIL | 0.5 |  |  | 81
18.10.24 | 7.79 | 26 |  | 0.5 | 1439 | 964 | 570 | 262 | 308 | 160 | 3.6 | - | NIL | 0.5 |  |  | 81
19.10.24 | 8.02 | 35 |  | 1 | 1664 | 1115 | 583 | 262 | 321 | 167 | 3.4 | - | NIL | 0.5 |  |  | 79
21.10.24 | 7.93 | 40 |  | 0.6 | 1559 | 1045 | 596 | 237 | 359 | 160 | 3.9 | - | NIL | 0.5 |  |  | 83
22.10.24 | 7.98 | 38 |  | NIL | 1683 | 1128 | 591 | 228 | 363 | 167 | 4.1 | - | NIL | 0.5 |  |  | 80
23.10.24 | 7.84 | 38 |  | 0.9 | 1714 | 1149 | 582 | 224 | 358 | 175 | 4.3 | - | NIL | 0.5 |  |  | 85
24.10.24 | 7.12 | 32 |  | 0.5 | 1673 | 1121 | 573 | 215 | 358 | 163 | 4.2 | - | NIL | 0.5 |  |  | 82
25.10.24 | 7.46 | 40 |  | 0.9 | 1862 | 1248 | 582 | 220 | 362 | 182 | 4.3 | - | NIL | 0.5 |  |  | 86
26.10.24 | 8.02 | 36 |  | NIL | 1668 | 1118 | 576 | 224 | 352 | 175 | 4.4 | - | NIL | 0.5 |  |  | 84
28.10.24 | 8.32 | 38 |  | NIL | 1623 | 1088 | 583 | 228 | 355 | 182 | 4.4 | - | NIL | 0.5 |  |  | 83
29.10.24 | 8.36 | 40 |  | NIL | 1431 | 959 | 605 | 224 | 381 | 175 | 4.3 | - | NIL | 0.5 |  |  | 85
30.10.24 | 7.51 | 32 |  | NIL | 1455 | 975 | 591 | 220 | 371 | 153 | 4.2 | - | NIL | 0.5 |  |  | 81
31.10.24 | 7.99 | 34 |  | NIL | 1429 | 958 | 568 | 220 | 348 | 167 | 4.4 | - | NIL | 0.5 |  |  | 83
04.11.24 | 8.02 | 30 |  | NIL | 1464 | 981 | 564 | 314 | 250 | 160 | 4.4 | - | NIL | 0.5 |  |  | 87
05.11.24 | 6.97 | 21 |  | 0.8 | 1597 | 1070 | 584 | 314 | 270 | 153 | 4.2 | - | NIL | 0.5 |  |  | 85
06.11.24 | 8.07 | 19 |  | 0.2 | 1585 | 1062 | 580 | 310 | 270 | 160 | 4.3 | - | NIL | 0.5 |  |  | 82
07.11.24 | 8.03 | 30 |  | 0.6 | 1679 | 1125 | 590 | 310 | 280 | 153 | 4.2 | - | NIL | 0.5 |  |  | 85
08.11.24 | 8.11 | 39 |  | 0.2 | 1558 | 1044 | 581 | 326 | 255 | 160 | 4.2 | - | NIL | 0.5 |  |  | 84
09.11.24 | 7.39 | 29 |  | 0.5 | 1453 | 974 | 590 | 317 | 273 | 153 | 4.1 | - | NIL | 0.5 |  |  | 86
11.11.24 | 8.07 | 28 |  | 0.4 | 1522 | 1020 | 572 | 295 | 277 | 153 | 3.8 | - | NIL | 0.5 |  |  | 80
12.11.24 | 7.98 | 25 |  | NIL | 1541 | 1033 | 538 | 269 | 269 | 160 | 3.6 | - | NIL | 0.5 |  |  | 83
13.11.24 | 8.41 | 31 |  | 1 | 1644 | 1102 | 541 | 270 | 271 | 153 | 3.8 | - | NIL | 0.5 |  |  | 81
14.11.24 | 8.06 | 25 |  | 0.7 | 1502 | 1007 | 782 | 262 | 520 | 166 | 3.5 | - | NIL | 0.5 |  |  | 80
15.11.24 | 8.34 | 27 |  | 0.4 | 1707 | 1144 | 574 | 254 | 320 | 153 | 3.4 | - | NIL | 0.5 |  |  | 83
16.11.24 | 7.86 | 27 |  | NIL | 1629 | 1092 | 582 | 254 | 328 | 160 | 3.2 | - | NIL | 0.5 |  |  | 81
18.11.24 | 8.49 | 27 |  | NIL | 1662 | 1114 | 582 | 258 | 324 | 160 | 3.3 | - | NIL | 0.5 |  |  | 83
19.11.24 | 8.39 | 27 |  | NIL | 1671 | 1120 | 591 | 170 | 421 | 167 | 3.4 | - | NIL | 0.5 |  |  | 83
20.11.24 | 8.25 | 27 |  | 0.2 | 1611 | 1080 | 595 | 262 | 333 | 160 | 3.2 | - | NIL | 0.5 |  |  | 83
21.11.24 | 8.24 | 20 |  | 0.8 | 1674 | 1122 | 587 | 250 | 337 | 153 | 3.5 | - | NIL | 0.5 |  |  | 85
22.11.24 | 8.24 | 21 |  | 0.6 | 1519 | 1018 | 595 | 258 | 337 | 146 | 3.3 | - | NIL | 0.5 |  |  | 89
23.11.24 | 8.5 | 22 |  | 1 | 1579 | 1058 | 596 | 256 | 340 | 167 | 3.4 | - | NIL | 0.5 |  |  | 82
25.11.24 | 8.48 | 21 |  | NIL | 1437 | 963 | 596 | 260 | 336 | 160 | 3.2 | - | NIL | 0.5 |  |  | 82
26.11.24 | 7.53 | 17 |  | 0.9 | 1496 | 1002 | 601 | 252 | 349 | 167 | 3.3 | - | NIL | 0.5 |  |  | 80
27.11.24 | 7.81 | 15 |  | 0.5 | 1473 | 987 | 588 | 244 | 344 | 160 | 3.5 | - | NIL | 0.5 |  |  | 86
28.11.24 | 8.31 | 19 |  | 0.4 | 1482 | 993 | 584 | 235 | 349 | 153 | 3.4 | - | NIL | 0.5 |  |  | 84
29.11.24 | 7.65 | 15 |  | NIL | 1428 | 957 | 575 | 239 | 336 | 160 | 3.3 | - | NIL | 0.5 |  |  | 83
30.11.24 | 7.17 | 16 |  | NIL | 1489 | 998 | 580 | 248 | 332 | 153 | 3.5 | - | NIL | 0.5 |  |  | 79
02.12.24 | 7.95 | 16 |  | NIL | 1474 | 988 | 601 | 260 | 341 | 160 | 3.2 | - | NIL | 0.5 |  |  | 82
03.12.24 | 7.82 | 16 |  | 0.6 | 1453 | 974 | 594 | 259 | 335 | 153 | 3.5 | - | NIL | 0.5 |  |  | 85
04.12.24 | 7.82 | 16 |  | NIL | 1414 | 948 | 606 | 263 | 343 | 160 | 3.2 | - | NIL | 0.5 |  |  | 83
05.12.24 | 7.78 | 15 |  | 0.1 | 1465 | 982 | 530 | 263 | 267 | 153 | 3.4 | - | NIL | 0.5 |  |  | 86
06.12.24 | 8.15 | 17 |  | 0.5 | 1588 | 1064 | 628 | 267 | 361 | 160 | 3.4 | - | NIL | 0.5 |  |  | 83
07.12.24 | 8.1 | 20 |  | 0.5 | 1448 | 970 | 668 | 349 | 319 | 138 | 3.5 | - | NIL | 0.5 |  |  | 90
09.12.24 | 8.15 | 15 |  | 0.2 | 1420 | 952 | 613 | 353 | 260 | 153 | 3.5 | - | NIL | 0.5 |  |  | 85
10.12.24 | 7.84 | 16 |  | 0.2 | 1525 | 1022 | 617 | 361 | 256 | 160 | 3.6 | - | NIL | 0.5 |  |  | 83
11.12.24 | 7.58 | 17 |  | 0.4 | 1478 | 990 | 613 | 357 | 256 | 160 | 3.4 | - | NIL | 0.5 |  |  | 86
12.12.24 | 7.09 | 18 |  | 0.2 | 1442 | 966 | 617 | 357 | 260 | 153 | 3.5 | - | NIL | 0.5 |  |  | 85
13.12.24 | 8.06 | 17 |  | 0.5 | 1479 | 991 | 622 | 357 | 265 | 160 | 3.6 | - | NIL | 0.5 |  |  | 81
14.12.24 | 7.56 | 20 |  | 0.4 | 1497 | 1003 | 607 | 349 | 258 | 153 | 3.2 | - | NIL | 0.5 |  |  | 85
16.12.24 | 7.46 | 19 |  | 0.6 | 1507 | 1010 | 581 | 336 | 245 | 156 | 3.1 | - | NIL | 0.5 |  |  | 84
17.12.24 | 7.85 | 19 |  | 0.5 | 1582 | 1060 | 593 | 342 | 251 | 160 | 3.1 | - | NIL | 0.5 |  |  | 84
18.12.24 | 8.03 | 23 |  | 0.6 | 1191 | 798 | 602 | 340 | 262 | 156 | 3.2 | - | NIL | 0.5 |  |  | 86
19.12.24 | 8.12 | 31 |  | 0.1 | 1595 | 1069 | 612 | 337 | 275 | 146 | 3.5 | - | NIL | 0.5 |  |  | 84
20.12.24 | 8.15 | 29 |  | NIL | 1685 | 1129 | 603 | 555 | 48 | 160 | 3.3 | - | NIL | 0.5 |  |  | 81
21.12.24 | 7.56 | 20 |  | NIL | 1646 | 1103 | 582 | 341 | 241 | 146 | 3.1 | - | NIL | 0.5 |  |  | 86
23.12.24 | 8.63 | 22 |  | 0.1 | 1579 | 1058 | 588 | 339 | 249 | 153 | 3.4 | - | NIL | 0.5 |  |  | 87
24.12.24 | 7.36 | 15 |  | NIL | 1471 | 986 | 596 | 343 | 253 | 168 | 3.3 | - | NIL | 0.5 |  |  | 82
25.12.24 | 8.01 | 21 |  | NIL | 1441 | 966 | 604 | 347 | 257 | 160 | 3.2 | - | NIL | 0.5 |  |  | 86
26.12.24 | 7.41 | 26 |  | NIL | 1538 | 1031 | 596 | 351 | 245 | 167 | 3.3 | - | NIL | 0.5 |  |  | 82
27.12.24 | 6.87 | 32 |  | 1 | 1726 | 1157 | 608 | 359 | 249 | 160 | 3.5 | - | NIL | 0.5 |  |  | 88
28.12.24 | 7.21 | 28 |  | 0.9 | 1649 | 1105 | 633 | 261 | 372 | 153 | 3.4 | - | NIL | 0.5 |  |  | 85
30.12.24 | 8.08 | 23 |  | 0.4 | 1785 | 1196 | 668 | 351 | 317 | 160 | 3.2 | - | NIL | 0.5 |  |  | 86
31.12.24 | 8.1 | 25 |  | 0.3 | 1758 | 1178 | 608 | 347 | 261 | 146 | 3.5 | - | NIL | 0.5 |  |  | 88
01.01.25 | 8.11 | 24 |  | NIL | 1597 | 1070 | 664 | 377 | 287 | 160 | 3.6 | - | NIL | 0.4 |  |  | 85
02.01.25 | 7.02 | 25 |  | NIL | 1653 | 1108 | 675 | 373 | 302 | 167 | 3.5 | - | NIL | 0.5 |  |  | 81
03.01.25 | 8.23 | 22 |  | NIL | 1670 | 1119 | 662 | 369 | 293 | 153 | 3.4 | - | NIL | 0.5 |  |  | 83
04.01.25 | 7.78 | 26 |  | NIL | 1652 | 1107 | 670 | 360 | 310 | 144 | 3.3 | - | NIL | 0.5 |  |  | 81
06.01.25 | 8.04 | 22 |  | NIL | 1701 | 1140 | 684 | 364 | 320 | 158 | 3.3 | - | NIL | 0.5 |  |  | 84
07.01.25 | 7.62 | 18 |  | NIL | 1671 | 1120 | 675 | 355 | 320 | 144 | 3.5 | - | NIL | 0.5 |  |  | 92
08.01.25 | 7.06 | 18 |  | NIL | 1640 | 1099 | 666 | 346 | 320 | 158 | 3.6 | - | NIL | 0.5 |  |  | 85
09.01.25 | 7.66 | 20 |  | NIL | 1568 | 1051 | 688 | 360 | 328 | 165 | 3.4 | - | NIL | 0.6 |  |  | 88
10.01.25 | 8.41 | 18 |  | NIL | 1600 | 1072 | 679 | 364 | 315 | 151 | 3.3 | - | NIL | 0.6 |  |  | 85
11.01.25 | 8.45 | 19 |  | NIL | 1600 | 1072 | 679 | 360 | 319 | 158 | 3.4 | - | NIL | 0.6 |  |  | 88
13.01.25 | 8.04 | 18 |  | NIL | 1544 | 1035 | 670 | 360 | 310 | 158 | 3.1 | - | NIL | 0.6 |  |  | 82
15.01.25 | 8.13 | 18 |  | 0.2 | 1653 | 1108 | 659 | 376 | 283 | 158 | 3.2 | - | NIL | 0.6 |  |  | 82
16.01.25 | 7.96 | 15 |  | NIL | 1634 | 1095 | 696 | 385 | 311 | 172 | 3.5 | - | NIL | 0.6 |  |  | 80
17.01.25 | 8.54 | 18 |  | NIL | 1523 | 1021 | 664 | 380 | 284 | 158 | 3.3 | - | NIL | 0.5 |  |  | 84
18.01.25 | 8.48 | 19 |  | NIL | 1604 | 1104 | 673 | 376 | 297 | 165 | 3.2 | - | NIL | 0.5 |  |  | 80
20.01.25 | 8.28 | 18 |  | NIL | 1592 | 1067 | 682 | 380 | 302 | 158 | 3.2 | - | NIL | 0.5 |  |  | 80
21.01.25 | 7.92 | 23 |  | NIL | 1610 | 1079 | 696 | 390 | 306 | 165 | 3.5 | - | NIL | 0.6 |  |  | 83
22.01.25 | 8.82 | 17 |  | NIL | 1628 | 1091 | 705 | 399 | 306 | 158 | 3.6 | - | NIL | 0.5 |  |  | 82
23.01.25 | 7.84 | 15 |  | NIL | 1631 | 1093 | 710 | 380 | 330 | 151 | 3.8 | - | NIL | 0.5 |  |  | 85
24.01.25 | 7.94 | 25 |  | 1 | 1547 | 1037 | 705 | 385 | 320 | 165 | 3.6 | - | NIL | 0.5 |  |  | 82
25.01.25 | 7.54 | 27 |  | NIL | 1658 | 1111 | 739 | 394 | 345 | 151 | 3.6 | - | NIL | 0.6 |  |  | 85
27.01.25 | 8.43 | 28 |  | NIL | 1550 | 1039 | 725 | 394 | 331 | 158 | 3.6 | - | NIL | 0.5 |  |  | 86
28.01.25 | 8.06 | 18 |  | NIL | 1652 | 1107 | 734 | 389 | 345 | 165 | 4.5 | - | NIL | 0.5 |  |  | 86
29.01.25 | 8.78 | 26 |  | NIL | 1788 | 1198 | 749 | 394 | 355 | 172 | 4.6 | - | NIL | 0.5 |  |  | 92
30.01.25 | 7.89 | 26 |  | 0.1 | 1604 | 1075 | 758 | 398 | 360 | 187 | 4.5 | - | NIL | 0.5 |  |  | 75
31.01.25 | 7.14 | 32 |  | 0.6 | 1561 | 1046 | 768 | 403 | 365 | 172 | 4.6 | - | NIL | 0.5 |  |  | 76
01.02.25 | 7.49 | 26 |  | 1 | 1564 | 1048 | 731 | 391 | 340 | 203 | 4.5 | - | NIL | 0.5 |  |  | 79
03.02.25 | 7.88 | 20 |  | NIL | 1535 | 1029 | 812 | 478 | 334 | 174 | 4.4 | - | NIL | 0.5 |  |  | 72
04.02.25 | 8.37 | 32 |  | NIL | 1538 | 1031 | 823 | 488 | 335 | 186 | 4.5 | - | NIL | 0.5 |  |  | 73
05.02.25 | 8.28 | 32 |  | NIL | 1510 | 1012 | 819 | 483 | 336 | 170 | 4.4 | - | NIL | 0.5 |  |  | 71
06.02.25 | 7.61 | 26 |  | 1 | 1522 | 1020 | 791 | 469 | 322 | 162 | 4.6 | - | NIL | 0.5 |  |  | 65
07.02.25 | 7.21 | 20 |  | 1 | 1573 | 1054 | 800 | 478 | 322 | 186 | 4.3 | - | NIL | 0.5 |  |  | 69
08.02.25 | 8.15 | 24 |  | 0.2 | 1652 | 1107 | 810 | 469 | 341 | 178 | 4.5 | - | NIL | 0.5 |  |  | 75
10.02.25 | 7.85 | 25 |  | 0.2 | 1635 | 1096 | 837 | 481 | 356 | 186 | 4.3 | - | NIL | 0.5 |  |  | 76
11.02.25 | 8.08 | 22 |  | 0.5 | 1564 | 1048 | 759 | 404 | 355 | 170 | 4.6 | - | NIL | 0.5 |  |  | 69
12.02.25 | 8.2 | 25 |  | 1 | 1603 | 1074 | 768 | 413 | 355 | 178 | 4.8 | - | NIL | 0.5 |  |  | 73
13.02.25 | 7.18 | 24 |  | 1 | 1764 | 1182 | 764 | 453 | 311 | 162 | 4.2 | - | NIL | 0.6 |  |  | 65
14.02.25 | 7.77 | 25 |  | 0.5 | 1614 | 1082 | 777 | 444 | 333 | 186 | 4.4 | - | NIL | 0.5 |  |  | 71
15.02.25 | 8.12 | 28 |  | 0.6 | 1882 | 1291 | 790 | 457 | 333 | 178 | 4.4 | - | NIL | 0.6 |  |  | 73
17.02.25 | 8.23 | 26 |  | NIL | 1840 | 1233 | 781 | 444 | 337 | 178 | 4.4 | - | NIL | 0.6 |  |  | 72
18.02.25 | 8.3 | 24 |  | 0.5 | 1792 | 1201 | 768 | 448 | 320 | 186 | 4.3 | - | NIL | 0.5 |  |  | 73
19.02.25 | 8.61 | 18 |  | 0.6 | 1647 | 1104 | 747 | 476 | 271 | 203 | 4.5 | - | NIL | 0.6 |  |  | 75
20.02.25 | 7.97 | 17 |  | 0.6 | 1725 | 1156 | 881 | 471 | 410 | 203 | 4.4 | - | NIL | 0.5 |  |  | 79
21.02.25 | 8.38 | 16 |  | 0.5 | 1556 | 1043 | 871 | 481 | 390 | 194 | 4.2 | - | NIL | 0.5 |  |  | 75
22.02.25 | 8.38 | 18 |  | NIL | 1620 | 1086 | 851 | 478 | 373 | 178 | 4.5 | - | NIL | 0.6 |  |  | 77
24.02.25 | 8.05 | 15 |  | NIL | 1488 | 997 | 819 | 460 | 359 | 158 | 4.3 | - | NIL | 0.6 |  |  | 74
25.02.25 | 8.01 | 21 |  | NIL | 1523 | 1021 | 805 | 465 | 340 | 187 | 4.5 | - | NIL | 0.5 |  |  | 70
27.02.25 | 7.45 | 18 |  | NIL | 1494 | 1001 | 769 | 423 | 346 | 180 | 4.6 | - | NIL | 0.5 |  |  | 65
28.02.25 | 8.3 | 15 |  | NIL | 1570 | 1052 | 756 | 428 | 328 | 172 | 4.2 | - | NIL | 0.5 |  |  | 70
01.03.25 | 8.02 | 16 |  | NIL | 1567 | 1050 | 760 | 428 | 332 | 165 | 4.3 | - | NIL | 0.6 |  |  | 72
03.03.25 | 8.79 | 19 |  | NIL | 1508 | 1011 | 691 | 680 | 11 | 169 | 4.2 | - | NIL | 0.5 |  |  | 77
04.03.25 | 8.49 | 21 |  | NIL | 1411 | 946 | 708 | 389 | 319 | 187 | 4.3 | - | NIL | 0.5 |  |  | 75
05.03.25 | 7.86 | 23 |  | 0.1 | 1304 | 874 | 713 | 376 | 337 | 178 | 4 | - | NIL | 0.6 |  |  | 76
06.03.25 | 8.18 | 19 |  | NIL | 1319 | 884 | 696 | 397 | 299 | 160 | 4.2 | - | NIL | 0.5 |  |  | 75
07.03.25 | 7.97 | 17 |  | NIL | 1497 | 1003 | 704 | 415 | 289 | 178 | 4 | - | NIL | 0.6 |  |  | 74
08.03.25 | 7.78 | 18 |  | NIL | 1380 | 925 | 717 | 424 | 293 | 169 | 4.2 | - | NIL | 0.5 |  |  | 69
10.03.25 | 7.64 | 18 |  | NIL | 1490 | 998 | 725 | 428 | 297 | 178 | 4.1 | - | NIL | 0.5 |  |  | 74
11.03.25 | 8.15 | 18 |  | NIL | 1513 | 1014 | 761 | 462 | 299 | 187 | 4.3 | - | NIL | 0.5 |  |  | 65
12.03.25 | 7.73 | 19 |  | NIL | 1389 | 931 | 783 | 466 | 317 | 195 | 4.3 | - | NIL | 0.5 |  |  | 71
13.03.25 | 7.41 | 18 |  | NIL | 1531 | 1026 | 796 | 449 | 347 | 178 | 4.5 | - | NIL | 0.6 |  |  | 75
15.03.25 | 8.06 | 20 |  | 0.2 | 1543 | 1034 | 796 | 458 | 338 | 187 | 4.5 | - | NIL | 0.6 |  |  | 70
17.03.25 | 7.82 | 16 |  | 0.5 | 1525 | 1022 | 669 | 528 | 141 | 187 | 4.5 | - | NIL | 0.5 |  |  | 70
18.03.25 | 7.76 | 21 |  | 0.3 | 1519 | 1018 | 704 | 383 | 321 | 213 | 4.6 | - | NIL | 0.6 |  |  | 72
19.03.25 | 8.15 | 23 |  | 0.5 | 1556 | 1043 | 717 | 392 | 325 | 204 | 4.7 | - | NIL | 0.5 |  |  | 73
20.03.25 | 8.02 | 23 |  | 0.5 | 1604 | 1075 | 726 | 396 | 330 | 222 | 4.6 | - | NIL | 0.5 |  |  | 76
21.03.25 | 8.09 | 15 |  | 0.5 | 1825 | 1223 | 717 | 392 | 325 | 213 | 4.5 | - | NIL | 0.5 |  |  | 72
22.03.25 | 7.98 | 31 |  | 0.8 | 1920 | 1287 | 739 | 405 | 334 | 231 | 4.6 | - | NIL | 0.6 |  |  | 75
24.03.25 | 8.12 | 25 |  | NIL | 1825 | 1223 | 730 | 409 | 321 | 213 | 4.4 | - | NIL | 0.5 |  |  | 70
25.03.25 | 7.97 | 20 |  | NIL | 1531 | 1026 | 731 | 423 | 308 | 195 | 4.5 | - | NIL | 0.5 |  |  | 75
26.03.25 | 8.27 | 18 |  | NIL | 1691 | 1133 | 745 | 437 | 308 | 135 | 4.6 | - | NIL | 0.5 |  |  | 68
27.03.25 | 7.48 | 18 |  | NIL | 1798 | 1205 | 759 | 432 | 327 | 171 | 4.5 | - | NIL | 0.5 |  |  | 72
28.03.25 | 7.21 | 16 |  | NIL | 1821 | 1220 | 750 | 419 | 331 | 164 | 4.5 | - | NIL | 0.5 |  |  | 70
29.03.25 | 7.91 | 23 |  | 0.4 | 1949 | 1306 | 759 | 432 | 327 | 158 | 4.4 | - | NIL | 0.5 |  |  | 73
31.03.25 | 7.85 | 20 |  | 1 | 1768 | 1185 | 727 | 423 | 304 | 144 | 4.3 | - | NIL | 0.4 |  |  | 69
01.04.25 | 8.2 | 25 |  | 0.6 | 1704 | 1142 | 722 | 382 | 340 | 252 | 4 | - | NIL | 0.5 |  |  | 81
02.04.25 | 8.39 | 18 |  | 0.4 | 1793 | 1201 | 736 | 391 | 345 | 268 | 4.1 | - | NIL | 0.4 |  |  | 85
03.04.25 | 8.44 | 17 |  | 0.4 | 2031 | 1361 | 768 | 414 | 354 | 244 | 4.3 | - | NIL | 0.4 |  |  | 79
04.04.25 | 7.93 | 26 |  | 0.5 | 2259 | 1514 | 791 | 431 | 360 | 260 | 4.2 | - | NIL | 0.5 |  |  | 82
05.04.25 | 8 | 22 |  | 0.6 | 2201 | 1475 | 782 | 428 | 354 | 236 | 4.4 | - | NIL | 0.5 |  |  | 80
07.04.25 | 7.6 | 20 |  | 0.4 | 2509 | 1681 | 777 | 400 | 377 | 236 | 4.3 | - | NIL | 0.4 |  |  | 76
08.04.25 | 8.27 | 16 |  | 0.1 | 2131 | 1428 | 736 | 423 | 313 | 252 | 4.4 | - | NIL | 0.5 |  |  | 82
09.04.25 | 8.66 | 19 |  | NIL | 2018 | 1352 | 782 | 455 | 327 | 284 | 4.2 | - | NIL | 0.4 |  |  | 79
10.04.25 | 7.63 | 21 |  | NIL | 2070 | 1387 | 805 | 460 | 345 | 292 | 4.3 | - | NIL | 0.5 |  |  | 82
11.04.25 | 7.19 | 20 |  | NIL | 2259 | 1514 | 791 | 437 | 354 | 267 | 4.4 | - | NIL | 0.5 |  |  | 75
12.04.25 | 8.07 | 22 |  | NIL | 2017 | 1352 | 810 | 451 | 359 | 275 | 4.5 | - | NIL | 0.5 |  |  | 78
14.04.25 | 8.28 | 22 |  | 0.2 | 1783 | 1195 | 787 | 429 | 358 | 267 | 4.3 | - | NIL | 0.5 |  |  | 76
15.04.25 | 8.72 | 21 |  | NIL | 1452 | 973 | 690 | 409 | 281 | 251 | 4.6 | - | NIL | 0.5 |  |  | 79
16.04.25 | 8.14 | 21 |  | NIL | 1662 | 1114 | 722 | 423 | 299 | 259 | 4.5 | - | NIL | 0.5 |  |  | 77
17.04.25 | 7.94 | 21 |  | 0.5 | 1844 | 1236 | 727 | 428 | 299 | 308 | 4.6 | - | NIL | 0.6 |  |  | 75
18.04.25 | 7.97 | 20 |  | 0.5 | 2153 | 1443 | 731 | 419 | 312 | 284 | 4.4 | - | NIL | 0.6 |  |  | 79
19.04.25 | 6.93 | 20 |  | 0.5 | 2066 | 1384 | 728 | 419 | 309 | 252 | 4.5 | - | NIL | 0.5 |  |  | 83
21.04.25 | 8.18 | 20 |  | 0.2 | 1902 | 1275 | 738 | 405 | 333 | 276 | 4.1 | - | NIL | 0.5 |  |  | 77
22.04.25 | 7.61 | 21 |  | 0.1 | 1932 | 1295 | 752 | 428 | 324 | 252 | 4.4 | - | NIL | 0.5 |  |  | 81
23.04.25 | 8.29 | 21 |  | 0.2 | 1901 | 1274 | 762 | 443 | 319 | 276 | 4.5 | - | NIL | 0.6 |  |  | 79
24.04.25 | 7.06 | 23 |  | NIL | 1755 | 1176 | 785 | 428 | 357 | 244 | 4.3 | - | NIL | 0.5 |  |  | 75
25.04.25 | 7.94 | 19 |  | NIL | 2443 | 1637 | 776 | 414 | 362 | 268 | 4.2 | - | NIL | 0.5 |  |  | 79
26.04.25 | 8.23 | 18 |  | NIL | 2062 | 1382 | 771 | 409 | 362 | 260 | 4.1 | - | NIL | 0.5 |  |  | 80
28.04.25 | 8.12 | 22 |  | NIL | 1953 | 1309 | 776 | 390 | 386 | 268 | 4.2 | - | NIL | 0.6 |  |  | 72
29.04.25 | 8.67 | 23 |  | NIL | 1565 | 1049 | 783 | 347 | 436 | 276 | 4.5 | - | NIL | 0.5 |  |  | 75
30.04.25 | 8.62 | 20 |  | NIL | 1723 | 1155 | 734 | 326 | 408 | 252 | 4.6 | - | NIL | 0.5 |  |  | 78
01.05.25 | 8.69 | 20 |  | 0.1 | 1579 | 1058 | 755 | 318 | 437 | 236 | 4.4 | - | - | 0.5 |  |  | 81
02.05.25 | 8.24 | 18 |  | 0.1 | 1557 | 1043 | 759 | 400 | 359 | 252 | 4.5 | - | - | 0.5 |  |  | 78
03.05.25 | 8.25 | 19 |  | 0.1 | 1425 | 955 | 755 | 396 | 359 | 244 | 4.4 | - | - | 0.5 |  |  | 75
05.05.25 | 8.26 | 18 |  | 0.2 | 1410 | 945 | 755 | 388 | 367 | 236 | 4.1 | - | - | 0.5 |  |  | 77
06.05.25 | 8.03 | 18 |  | 0.4 | 1365 | 915 | 714 | 375 | 339 | 228 | 4.3 | - | - | 0.5 |  |  | 79
07.05.25 | 8.13 | 21 |  | 0.4 | 1380 | 925 | 726 | 379 | 347 | 236 | 4.5 | - | - | 0.5 |  |  | 81
08.05.25 | 8.4 | 19 |  | 0.1 | 1324 | 887 | 649 | 352 | 297 | 197 | 4.2 | - | - | 0.5 |  |  | 75
09.05.25 | 8.32 | 18 |  | 0.2 | 1120 | 753 | 642 | 337 | 305 | 181 | 4 | - | - | 0.4 |  |  | 70
10.05.25 | 8.04 | 18 |  | 0.2 | 1194 | 800 | 638 | 333 | 305 | 177 | 4.1 | - | - | 0.5 |  |  | 72
12.05.25 | 8.31 | 20 |  | Nil | 1070 | 717 | 741 | 325 | 416 | 197 | 4 | - | - | 0.4 |  |  | 75
13.05.25 | 8.33 | 23 |  | Nil | 1332 | 893 | 701 | 380 | 321 | 181 | 4.1 | - | - | 0.5 |  |  | 79
14.05.25 | 7.92 | 25 |  | 0.2 | 1237 | 829 | 673 | 388 | 285 | 205 | 4.6 | - | - | 0.6 |  |  | 83
15.05.25 | 7.56 | 19 |  | 0.2 | 1282 | 859 | 685 | 392 | 293 | 213 | 4.2 | - | - | 0.5 |  |  | 80
16.05.25 | 8.14 | 18 |  | Nil | 1145 | 767 | 681 | 376 | 305 | 181 | 4.1 | - | - | 0.5 |  |  | 83
17.05.25 | 8.16 | 20 |  | Nil | 1217 | 816 | 673 | 370 | 303 | 177 | 4.1 | - | - | 0.5 |  |  | 79
19.05.25 | 8.28 | 17 |  | Nil | 1038 | 696 | 664 | 361 | 303 | 165 | 4.3 | - | - | 0.5 |  |  | 79
20.05.25 | 8.54 | 21 |  | Nil | 1028 | 689 | 673 | 365 | 308 | 175 | 4.1 | - | - | 0.5 |  |  | 81
21.05.25 | 8.97 | 19 |  | 0.1 | 1143 | 766 | 686 | 374 | 312 | 188 | 4.2 | - | - | 0.5 |  |  | 78
22.05.25 | 7.88 | 18 |  | Nil | 1022 | 685 | 572 | 326 | 246 | 165 | 4 | - | - | 0.5 |  |  | 80
23.05.25 | 8.63 | 22 |  | Nil | 1167 | 782 | 581 | 343 | 238 | 162 | 4.2 | - | - | 0.4 |  |  | 83
24.05.25 | 8.71 | 18 |  | Nil | 1111 | 745 | 594 | 330 | 264 | 155 | 4 | - | - | 0.5 |  |  | 81
26.05.25 | 8.41 | 20 |  | 0.1 | 1402 | 940 | 598 | 326 | 272 | 166 | 4.2 | - | - | 0.4 |  |  | 77
27.05.25 | 8.01 | 20 |  | Nil | 1182 | 792 | 594 | 321 | 273 | 162 | 4.1 | - | - | 0.4 |  |  | 81
28.05.25 | 8.18 | 25 |  | Nil | 1152 | 772 | 616 | 326 | 290 | 170 | 4.1 | - | - | 0.5 |  |  | 79
29.05.25 | 8.18 | 19 |  | Nil | 1023 | 686 | 594 | 334 | 260 | 173 | 4.2 | - | - | 0.5 |  |  | 82
30.05.25 | 8.25 | 22 |  | Nil | 1247 | 836 | 598 | 321 | 277 | 165 | 4 | - | - | 0.4 |  |  | 85
31.05.25 | 8.18 | 19 |  | Nil | 1023 | 686 | 594 | 334 | 260 | 173 | 4.2 | - | - | 0.5 |  |  | 82
02.06.25 | 7.99 | 18 |  | Nil | 888 | 595 | 594 | 332 | 262 | 162 | 4.2 | - | - | 0.5 |  |  | 76
03.06.25 | 8.15 | 23 |  | 0.2 | 1085 | 727 | 603 | 342 | 261 | 158 | 4.3 | - | - | 0.5 |  |  | 84
04.06.25 | 8.3 | 21 |  | Nil | 902 | 605 | 514 | 325 | 189 | 165 | 4.5 | - | - | 0.5 |  |  | 85
05.06.25 | 8.27 | 20 |  | Nil | 938 | 629 | 538 | 340 | 198 | 187 | 4.6 | - | - | 0.4 |  |  | 80
06.06.25 | 8.32 | 18 |  | Nil | 976 | 654 | 547 | 345 | 202 | 172 | 4.5 | - | - | 0.5 |  |  | 83
07.06.25 | 8.56 | 20 |  | 0.5 | 907 | 608 | 560 | 332 | 228 | 158 | 4.2 | - | - | 0.5 |  |  | 79
09.06.25 | 8.7 | 23 |  | Nil | 1283 | 860 | 538 | 307 | 231 | 162 | 4.5 | - | - | 0.5 |  |  | 76
10.06.25 | 7.89 | 22 |  | 0.2 | 1356 | 909 | 523 | 301 | 222 | 158 | 4.2 | - | - | 0.4 |  |  | 72
11.06.25 | 8.02 | 25 |  | 0.8 | 1328 | 890 | 507 | 305 | 202 | 144 | 4.3 | - | - | 0.5 |  |  | 77
12.06.25 | 7.7 | 49 | 35 | Nil | 1100 | 737 | 439 | 271 | 168 | 244 | 6 | - | - | 0.3 |  |  | -
13.06.25 | 8.2 | 43 | - | Nil | 1050 | 703 | 422 | 263 | 159 | 246 | 6.3 | - | - | 0.3 |  |  | -
14.06.25 | 8.5 | - | 20 | Nil | 1068 | 715 | 430 | 268 | 162 | 249 | 6 | - | - | 0.3 |  |  | -
16.06.25 | 8.1 | - | 31 | 1 | 1042 | 698 | 412 | 254 | 158 | 262 | 6.4 | - | - | 0.3 |  |  | -
17.06.25 | 8.3 | - | 27 | Nil | 1038 | 690 | 380 | 238 | 142 | 213 | 5.7 | 95 | - | 0.3 |  |  | -
18.06.25 | 8.88 | - | 18 | 0.8 | 1374 | 921 | 562 | 371 | 191 | 180 | 4.5 | - | - | 0.5 |  |  | 72
19.06.25 | 8.33 | - | 19 | Nil | 1426 | 956 | 571 | 362 | 209 | 186 | 4.3 | - | - | 0.5 |  |  | 70
20.06.25 | 8.34 | - | 18 | Nil | 1365 | 915 | 569 | 362 | 207 | 178 | 4.2 | - | - | 0.5 |  |  | 72
21.06.25 | 8.5 | - | 19 | Nil | 1308 | 877 | 566 | 367 | 199 | 171 | 4 | - | - | 0.5 |  |  | 75
23.06.25 | 8.59 | - | 19 | Nil | 1156 | 775 | 555 | 362 | 193 | 186 | 4.2 | - | - | 0.4 |  |  | 77
24.06.25 | 7.84 | - | 20 | Nil | 1177 | 789 | 562 | 352 | 210 | 178 | 4.3 | - | - | 0.5 |  |  | 75
25.06.25 | 7.44 | - | 16 | Nil | 1355 | 908 | 588 | 328 | 260 | 171 | 4.2 | - | - | 0.5 |  |  | 78
26.06.25 | 7.3 | - | 18 | Nil | 1141 | 765 | 596 | 319 | 277 | 182 | 4.6 | - | - | 0.5 |  |  | 82
27.06.25 | 7.89 | - | 21 | Nil | 1217 | 816 | 617 | 315 | 302 | 175 | 4.3 | - | - | 0.4 |  |  | 81
28.06.25 | 8.1 | - | 17 | Nil | 1273 | 853 | 613 | 311 | 302 | 164 | 4.2 | - | - | 0.5 |  |  | 79
30.06.25 | 8.78 | - | 21 | Nil | 1374 | 921 | 619 | 318 | 301 | 171 | 4.2 | - | - | 0.5 |  |  | 78
01.07.25 | 7.01 | - | 20 | 0.5 | 1307 | 876 | 615 | 314 | 301 | 164 | 4.3 | - | - | 0.5 |  |  | 72
02.07.25 | 7.5 | - | 19 | Nil | 1485 | 995 | 636 | 322 | 314 | 178 | 4.4 | - | - | 0.5 |  |  | 78
03.07.25 | 7.71 | - | 18 | Nil | 1279 | 857 | 649 | 331 | 318 | 177 | 4.6 | - | - | 0.5 |  |  | 80
04.07.25 | 7.66 | - | 17 | Nil | 1268 | 850 | 644 | 322 | 322 | 187 | 4.5 | - | - | 0.5 |  |  | -
05.07.25 | 7.29 | - | 19 | Nil | 1025 | 687 | 636 | 374 | 262 | 203 | 4.2 | - | - | 0.5 |  |  | 88
07.07.25 | 7.5 | - | 18 | Nil | 1319 | 884 | 670 | 305 | 365 | 185 | 4.1 | - | - | 0.5 |  |  | 79
08.07.25 | 7.98 | - | 20 | 0.1 | 1313 | 880 | 661 | 310 | 351 | 174 | 4.3 | - | - | 0.5 |  |  | 78
09.07.25 | 8.38 | - | 15 | 0.2 | 1364 | 914 | 678 | 318 | 360 | 196 | 4.2 | - | - | 0.5 |  |  | 75
10.07.25 | 7.49 | - | 16 | 1 | 1268 | 850 | 691 | 314 | 377 | 189 | 4.1 | - | - | 0.5 |  |  | 79
11.07.25 | 7.65 | - | 19 | 0.5 | 1459 | 978 | 712 | 318 | 394 | 182 | 4.3 | - | - | 0.5 |  |  | 85
12.07.25 | 8.12 | - | 23 | Nil | 1838 | 1232 | 700 | 305 | 395 | 204 | 4.5 | - | - | 0.5 |  |  | 78
14.07.25 | 8.05 | - | 21 | 0.1 | 1792 | 1201 | 700 | 310 | 390 | 196 | 4.4 | - | - | 0.5 |  |  | 76
15.07.25 | 8.16 | - | 20 | 1 | 1880 | 1260 | 695 | 314 | 381 | 182 | 4.3 | - | - | 0.5 |  |  | 79
16.07.25 | 8.23 | - | 19 | Nil | 1731 | 1160 | 806 | 420 | 386 | 218 | 4.5 | - | - | 0.5 |  |  | 72
17.07.25 | 7.84 | - | 19 | Nil | 1792 | 1201 | 814 | 403 | 411 | 233 | 4.2 | - | - | 0.5 |  |  | 76
18.07.25 | 7.89 | - | 22 | 1 | 1874 | 1256 | 838 | 402 | 436 | 254 | 4.4 | - | - | 0.5 |  |  | 79
19.07.25 | 6.5 | - | 19 | 0.2 | 1734 | 1162 | 829 | 406 | 423 | 247 | 4.5 | - | - | 0.5 |  |  | 82
21.07.25 | 8.05 | - | 18 | Nil | 1741 | 1167 | 855 | 408 | 447 | 249 | 4.5 | - | - | 0.5 |  |  | 73
22.07.25 | 7.52 | - | 20 | Nil | 1491 | 999 | 847 | 406 | 441 | 241 | 4.4 | - | - | 0.4 |  |  | 72
23.07.25 | 8.44 | - | 25 | Nil | 1629 | 1092 | 864 | 471 | 393 | 227 | 4.5 | - | - | 0.5 |  |  | 78
24.07.25 | 8.05 | - | 19 | Nil | 1500 | 1005 | 855 | 467 | 388 | 234 | 4.6 | - | - | 0.4 |  |  | 75
25.07.25 | 8.32 | - | 22 | Nil | 1588 | 1064 | 851 | 454 | 397 | 249 | 4.5 | - | - | 0.5 |  |  | 82
26.07.25 | 8.46 | - | 22 | Nil | 1473 | 987 | 864 | 467 | 397 | 270 | 4.5 | - | - | 0.5 |  |  | 87
28.07.25 | 8.43 | - | 39 | 0.6 | 1325 | 888 | 868 | 462 | 406 | 263 | 4.5 | - | - | 0.5 |  |  | 84
29.07.25 | 8.35 | - | 25 | 0.8 | 1420 | 952 | 883 | 465 | 418 | 249 | 4.2 | - | - | 0.5 |  |  | 78
30.07.25 | 7.98 | - | 22 | 0.6 | 1717 | 1151 | 998 | 529 | 469 | 256 | 4.2 | - | - | 0.5 |  |  | 80
31.07.25 | 7.96 | - | 21 | 0.5 | 1463 | 980 | 897 | 506 | 391 | 263 | 4.3 | - | - | 0.5 |  |  | 76
01.08.25 | 7.61 | - | 18 | NIL | 1704 | 1142 | 919 | 514 | 405 | 249 | 4.5 | - | - | 0.4 |  |  | 83
02.08.25 | 7.8 | - | 18 | NIL | 1662 | 1114 | 909 | 500 | 409 | 234 | 4.5 | - | - | 0.5 |  |  | 80
04.08.25 | 8.39 | - | 19 | NIL | 1231 | 825 | 904 | 492 | 412 | 287 | 4.2 | - | - | 0.4 |  |  | 79
05.08.25 | 7.75 | - | 19 | NIL | 1314 | 881 | 900 | 486 | 414 | 208 | 4.3 | - | - | 0.5 |  |  | 75
06.08.25 | 8.1 | - | 18 | NIL | 1479 | 984 | 914 | 500 | 414 | 230 | 4.4 | - | - | 0.5 |  |  | 78
07.08.25 | 8.16 | - | 18 | NIL | 1316 | 882 | 909 | 505 | 404 | 223 | 4.5 | - | - | 0.4 |  |  | 75
08.08.25 | 8.4 | - | 18 | NIL | 1375 | 921 | 907 | 509 | 398 | 215 | 4.4 | - | - | 0.5 |  |  | 80
11.08.25 | 8.47 | - | 18 | NIL | 1543 | 1034 | 904 | 486 | 418 | 201 | 4.3 | - | - | 0.4 |  |  | 76
12.08.25 | 8.35 | - | 20 | NIL | 1574 | 1055 | 909 | 495 | 414 | 215 | 4.2 | - | - | 0.4 |  |  | 78
13.08.25 | 8.29 | - | 19 | NIL | 1570 | 1052 | 881 | 490 | 391 | 230 | 4.1 | - | - | 0.5 |  |  | 76
14.08.25 | 7.63 | - | 18 | 1 | 1592 | 1067 | 885 | 500 | 385 | 237 | 4.3 | - | - | 0.5 |  |  | 72
15.08.25 | 8.12 | - | 20 | 1 | 1671 | 1120 | 890 | 505 | 385 | 230 | 4.1 | - | - | 0.5 |  |  | 76
18.08.25 | 7.89 | - | 21 | 0.1 | 1625 | 1098 | 895 | 495 | 400 | 250 | 4.1 | - | - | 0.5 |  |  | 75
19.08.25 | 7.82 | - | 20 | 0.1 | 1574 | 1055 | 890 | 493 | 397 | 249 | 4.2 | - | - | 0.4 |  |  | 72
20.08.25 | 8.48 | - | 17 | 0.5 | 2238 | 1500 | 855 | 500 | 355 | 241 | 4.3 | - | - | 0.5 |  |  | 74
21.08.25 | 7.53 | - | 20 | 1 | 1979 | 1326 | 857 | 490 | 367 | 227 | 4 | - | - | 0.5 |  |  | 73
22.08.25 | 7.84 | - | 18 | 0.2 | 1232 | 826 | 871 | 495 | 376 | 256 | 4.1 | - | - | 0.5 |  |  | 75
23.08.25 | 8.14 | - | 18 | NIL | 1565 | 1049 | 881 | 490 | 391 | 249 | 4 | - | - | 0.5 |  |  | 79
25.08.25 | 8.36 | - | 19 | 0.1 | 1595 | 1069 | 870 | 486 | 384 | 227 | 4 | - | - | 0.5 |  |  | 71
26.08.25 | 8.17 | - | 18 | 0.8 | 1420 | 852 | 869 | 457 | 412 | 234 | 4.2 | - | - | 0.5 |  |  | 75
27.08.25 | 8.02 | - | 22 | 0.9 | 1328 | 890 | 739 | 470 | 269 | 220 | 4.3 | - | - | 0.5 |  |  | 79
28.08.25 | 8.11 | - | 21 | 0.6 | 1285 | 861 | 762 | 443 | 319 | 206 | 4.4 | - | - | 0.6 |  |  | 81
29.08.25 | 8.08 | - | 19 | 1 | 1410 | 945 | 744 | 486 | 258 | 220 | 4.2 | - | - | 0.5 |  |  | 78
MIN. | 5.68 | 17 |  | 0.1 | 888 | 595 | 380 | 138 | 11 | 142 | 5.8 | 95 | 0 | 0.3 | 0 | 0 | 65
MAX. | 8.97 | 28 |  | 1 | 2509 | 1681 | 998 | 680 | 520 | 368 | 10.5 | 95 | 0 | 0.6 | 0 | 0 | 96
AVG. | 7.9704 | 19 |  | 0.50338 | 1493.0244 | 1000.497 | 674.9512 | 356.8689 | 318.0823 | 197.3313 | 4.0512 | 95 | 0 | 0.49969 |  |  | 79.2329
No. of < Spec | 48 | -- |  | 19 | -- | -- | -- | -- | -- | -- | 324 | -- | -- | -- | -- | -- | --
No. of > Spec | 175 | 159 |  | 57 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 14.6341 | -- |  | 12.8378 | -- | -- | -- | -- | -- | -- | 98.7805 | [5 empty] | --
% > Specs. | 53.3537 | 60.2273 |  | 38.5135 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  |  | 0