## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SULFATE | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | 10 to 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2018-09-05 | 8.29 | 120 | 0.1 | 618 | 197 | 121 | 76 | 139 | 7.3 | 10.3 | 118 | 230 | 103
2018-09-06 | 8.34 | 63 | 0.1 | 634 | 210 | 130 | 80 | 140 | 7.4 | 10.4 | 120 | 233 | 105
2018-09-07 | 8.33 | 54 | 0.1 | 834 | 328 | 168 | 160 | 146 | 7.9 | 10.9 | 122 | 220 | 122
2018-09-08 | 8.14 | 24 | 0.1 | 1030 | 336 | 176 | 160 | 154 | 8 | 10.9 | 118 | 280 | 125
2018-09-09 | 8 | 25 | 0.1 | 1080 | 380 | 236 | 144 | 196 | 7.8 | 10.8 | 120 | 310 | 128
2018-09-10 | 7.9 | 25 | 0.1 | 1160 | 510 | 275 | 235 | 258 | 7.2 | 10.2 | 122 | 360 | 134
2018-09-11 | 7.85 | 26 | 0.1 | 1188 | 496 | 269 | 227 | 256 | 7 | 11 | 120 | 340 | 132
2018-09-12 | 7.67 | 15 | 0.1 | 1260 | 563 | 302 | 261 | 253 | 7.7 | 10.7 | 115 | 295 | 130
2018-09-13 | 7.64 | 19 | 0.1 | 1120 | 518 | 284 | 234 | 260 | 7.4 | 10.4 | 120 | 344 | 128
2018-09-14 | 7.52 | 18 | 0.1 | 1115 | 504 | 273 | 231 | 253 | 7.4 | 10.4 | 118 | 220 | 124
2018-09-15 | 7.78 | 16 | 0.1 | 1390 | 554 | 294 | 260 | 268 | 7.2 | 10.2 | 118 | 290 | 129
2018-09-16 | 7.8 | 15 | 0.1 | 1360 | 510 | 275 | 235 | 282 | 7 | 10.2 | 120 | 300 | 128
2018-09-17 | 7.79 | 15 | 0.1 | 1294 | 491 | 269 | 222 | 304 | 6.9 | 10.9 | 127 | 310 | 128
2018-09-18 | 8.12 | 15 | 0.1 | 1375 | 503 | 278 | 225 | 310 | 6.8 | 10.8 | 129 | 480 | 133
2018-09-19 | 8.16 | 14 | 0.1 | 1194 | 500 | 290 | 210 | 246 | 6.6 | 10.6 | 128 | 314 | 137
2018-09-20 | 8.1 | 15 | 0.1 | 1210 | 520 | 299 | 221 | 247 | 7 | 11 | 130 | 318 | 139
2018-09-21 | 7.39 | 14 | 0.1 | 1530 | 570 | 330 | 240 | 312 | 6.8104 | 10.8 | 125 | 489 | 140
2018-09-22 | 7.37 | 13 | 0.1 | 1507 | 567 | 328 | 239 | 311 | 6.9 | 10.9 | 124 | 393 | 139
2018-09-23 | 7.82 | 16 | 0.1 | 1510 | 560 | 320 | 240 | 319 | 6.8 | 10.8 | 120 | 382 | 140
2018-09-24 | 7.73 | 15 | 0.1 | 1493 | 552 | 318 | 234 | 310 | 6.8 | 10.8 | 118 | 380 | 140
2018-09-25 | 7.48 | 16 | 0.1 | 1720 | 756 | 376 | 380 | 377 | 6.9 | 10.9 | 112 | 344 | 139
2018-09-26 | 7.5 | 14 | 0.1 | 1830 | 760 | 384 | 376 | 380 | 6.7 | 10.7 | 120 | 470 | 142
2018-09-27 | 7.62 | 16 | 0.1 | 2014 | 899 | 484 | 415 | 471 | 6.6 | 10.6 | 118 | 468 | 146
2018-09-28 | 7.54 | 16 | 0.1 | 2030 | 909 | 490 | 419 | 474 | 6.9 | 10.9 | 124 | 869 | 148
2018-09-29 | 7.51 | 18 | 0.2 | 1740 | 847 | 462 | 385 | 343 | 6.8 | 10.8 | 119 | 723 | 149
2018-09-30 | 7.54 | 17 | 0.1 | 1692 | 828 | 452 | 376 | 328 | 6.7 | 10.7 | 120 | 720 | 150
MIN. | 7.37 | 13 | 0.1 | 618 | 197 | 121 | 144 | 139 | 6.6 | 10.2 | 112 | 220 | 103
MAX. | 8.34 | 120 | 0.2 | 2030 | 909 | 490 | 419 | 474 | 8 | 11 | 130 | 869 | 150
AVG. | 7.805 | 24.3846 | 0.10385 | 1343.3846 | 552.6154 | 303.1923 | 268.2174 | 282.1923 | 7.0966 | 10.6769 | 120.9615 | 387.7692 | 133
No. of < Spec | 3 | 19 | 25 | 26 | 26 | 26 | 24 | 26 | 0 | 0 | 26 | 26 | 26
No. of > Spec | 7 | 7 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
% < Specs. | 11.5385 | 73.0769 | 96.1538 | 100 | 100 | 100 | 92.3077 | 100 | 0 | 0 | 100 | 100 | 100
% > Specs. | 26.9231 | 26.9231 | 0 | 0 | 0 | 0 | 7.6923 | 0 | 0 | 0 | 0 | 0 | 0
CIRCULATING WATER ANALYSIS FOR COOLING TOWER
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SULFATE | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | 10 to 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2018-09-01 | - | - | - | SHUT | DOWN | - | - | - | - | - | - | - | -
2018-09-02 | - | - | - | BASIN IS | CLEANING | - | - | - | - | - | - | - | -
2018-09-03 | - | - | - | - | - | - | - | - | - | - | - | - | -
2018-09-04 | - | - | - | - | - | - | - | - | - | - | - | - | -