## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SULFATE | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | 10 to 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2019-12-01 | 7.9 | 21 | 0.1 | 1398 | 706 | 420 | 286 | 240 | 6.6 | 10.6 | 122 | 868 | 154
2019-12-02 | 7.96 | 22 | 0.1 | 1410 | 710 | 428 | 282 | 242 | 6.7 | 10.7 | 124 | 870 | 156
2019-12-03 | 8 | 25 | 0.1 | 1480 | 722 | 441 | 281 | 281 | 6.7 | 10.7 | 128 | 892 | 153
2019-12-04 | 7.45 | 22 | 0.1 | 1300 | 704 | 433 | 271 | 249 | 6.9 | 10.9 | 118 | 870 | 155
2019-12-05 | 8.02 | 18 | 0.2 | 1237 | 706 | 424 | 282 | 245 | 6.8 | 10.8 | 119 | 860 | 154
2019-12-06 | 7.98 | 20 | 0.1 | 1282 | 704 | 420 | 284 | 246 | 6.6 | 10.6 | 120 | 866 | 154
2019-12-07 | 7.88 | 22 | 0.1 | 1322 | 706 | 424 | 282 | 248 | 6.6 | 10.6 | 120 | 868 | 154
2019-12-08 | 7.87 | 28 | 0.1 | 1380 | 705 | 398 | 307 | 249 | 6.5 | 10.6 | 118 | 874 | 156
2019-12-09 | 7.84 | 32 | 0.1 | 1483 | 706 | 374 | 332 | 249 | 6.5 | 10.5 | 119 | 879 | 158
2019-12-10 | 7.9 | 34 | 0.1 | 1590 | 714 | 378 | 336 | 257 | 6.8 | 10.8 | 118 | 872 | 165
2019-12-11 | 8.02 | 28 | 0.1 | 1570 | 731 | 433 | 298 | 345 | 6.9 | 10.9 | 129 | 860 | 150
2019-12-12 | 7.56 | 34 | 0.2 | 1610 | 739 | 441 | 298 | 349 | 7 | 11 | 123 | 872 | 156
2019-12-13 | 7.39 | 35 | 0.2 | 1710 | 748 | 458 | 290 | 353 | 6.5 | 10.5 | 110 | 880 | 158
2019-12-14 | 7.9 | 33 | 0.1 | 1722 | 759 | 464 | 295 | 355 | 7 | 11 | 128 | 870 | 160
2019-12-15 | 7.82 | 28 | 0.1 | 1650 | 740 | 352 | 388 | 310 | 6.8 | 10.8 | 120 | 868 | 160
16/12/19 | 7.8 | 26 | 0.1 | 1420 | 748 | 356 | 392 | 284 | 6.7 | 10.7 | 120 | 864 | 160
2019-12-17 | 7.7 | 24 | 0.1 | 1340 | 731 | 349 | 382 | 245 | 6.6 | 10.6 | 119 | 860 | 162
2019-12-18 | 7.88 | 26 | 0.1 | 1390 | 739 | 357 | 382 | 253 | 6.4 | 10.4 | 128 | 860 | 160
2019-12-19 | 7.62 | 34 | 0.1 | 1270 | 731 | 349 | 382 | 245 | 6.8 | 10.8 | 113 | 866 | 158
2019-12-20 | 7.98 | 30 | 0.2 | 1140 | 739 | 357 | 382 | 250 | 6.9 | 10.9 | 124 | 879 | 150
2019-12-21 | 7.73 | 36 | 0.1 | 1134 | 731 | 349 | 382 | 249 | 6.6 | 10.6 | 119 | 866 | 148
2019-12-22 | 7.78 | 34 | 0.1 | 1280 | 742 | 356 | 386 | 252 | 6.8 | 10.8 | 116 | 872 | 152
2019-12-23 | 7.84 | 30 | 0.1 | 1310 | 752 | 370 | 382 | 261 | 7 | 11 | 114 | 880 | 158
2019-12-24 | 8.04 | 35 | 0.1 | 1280 | 651 | 378 | 273 | 249 | 6.7 | 10.7 | 128 | 870 | 150
2019-12-25 | 7.7 | 38 | 0.1 | 1250 | 659 | 386 | 273 | 253 | 6.5 | 10.5 | 120 | 860 | 152
2019-12-26 | 7.75 | 34 | 0.1 | 1274 | 650 | 380 | 270 | 250 | 6.9 | 10.9 | 118 | 872 | 148
2019-12-27 | 8.1 | 19 | 0.1 | 1410 | 697 | 378 | 319 | 261 | 6.7 | 10.7 | 128 | 878 | 155
2019-12-28 | 8.02 | 20 | 0.1 | 1428 | 710 | 392 | 318 | 263 | 6.9 | 10.9 | 130 | 880 | 154
2019-12-29 | 8.01 | 18 | 0.1 | 1380 | 662 | 382 | 280 | 248 | 6.7 | 10.7 | 128 | 835 | 150
2019-12-30 | 8.06 | 18 | 0.1 | 1310 | 563 | 326 | 237 | 238 | 6.8 | 10.8 | 122 | 814 | 150
2019-12-31 | 8.09 | 16 | 0.1 | 1210 | 571 | 335 | 236 | 215 | 6.8 | 10.8 | 135 | 810 | 155
MIN. | 7.39 | 16 | 0.1 | 1134 | 563 | 326 | 237 | 215 | 6.4 | 10.4 | 110 | 810 | 146
MAX. | 8.1 | 38 | 0.2 | 1722 | 759 | 464 | 392 | 355 | 7 | 11 | 135 | 892 | 142
AVG. | 7.8577 | 27.0968 | 0.1129 | 1386.129 | 705.6774 | 389.9355 | 331.0556 | 265.6129 | 6.7323 | 10.7355 | 121.871 | 865.6452 | 155
No. of < Spec | 2 | 5 | 27 | 31 | 31 | 31 | 31 | 31 | 0 | 0 | 31 | 31 | 31
No. of > Spec | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
% < Specs. | 6.4516 | 16.129 | 87.0968 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 100
% > Specs. | 25.8065 | 77.4194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0