## Sheet1
CIRCULATING WATER ANALYSIS FOR X 01 COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SO4-2 | SiO2
| 7.5 - 8.3 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2019-12-01 | 8.02 | 36 | 0.2 | 770 | 580 | 353 | 227 | 138 | 6.5 | 10.5 | 130 | 862 | 150
2019-12-02 | 7.98 | 35 | 0.1 | 784 | 589 | 340 | 249 | 140 | 6.5 | 10.6 | 128 | 864 | 152
2019-12-03 | 8.15 | 30 | 0.1 | 740 | 571 | 349 | 222 | 142 | 6.9 | 10.9 | 133 | 876 | 148
2019-12-04 | 8.09 | 29 | 0.1 | 753 | 563 | 340 | 223 | 144 | 6.9 | 10.9 | 130 | 874 | 146
2019-12-05 | 7.8 | 25 | 0.2 | 660 | 554 | 332 | 222 | 130 | 6.6 | 10.6 | 119 | 864 | 145
2019-12-06 | 7.9 | 25 | 0.2 | 739 | 550 | 330 | 220 | 133 | 6.5 | 10.5 | 133 | 852 | 148
2019-12-07 | 7.9 | 33 | 0.1 | 740 | 525 | 281 | 244 | 118 | 6.3 | 10.3 | 130 | 820 | 150
2019-12-08 | 7.98 | 34 | 0.1 | 758 | 540 | 293 | 247 | 112 | 6.4 | 10.4 | 133 | 818 | 150
2019-12-09 | 7.78 | 35 | 0.2 | 719 | 521 | 277 | 244 | 104 | 6.2 | 10.2 | 133 | 830 | 133
2019-12-10 | 7.88 | 34 | 0.2 | 733 | 509 | 270 | 239 | 104 | 6.2 | 10.2 | 135 | 832 | 135
2019-12-11 | 7.9 | 32 | 0.2 | 870 | 441 | 302 | 139 | 107 | 6.8 | 10.8 | 140 | 810 | 140
2019-12-12 | 7.6 | 29 | 0.2 | 1087 | 460 | 320 | 140 | 116 | 6.7 | 10.7 | 122 | 822 | 145
2019-12-13 | 7.7 | 21 | 0.1 | 648 | 480 | 343 | 137 | 123 | 6.8 | 10.8 | 120 | 832 | 150
2019-12-14 | 7.72 | 24 | 0.1 | 684 | 480 | 340 | 140 | 128 | 6.8 | 10.8 | 128 | 840 | 154
2019-12-15 | 7.89 | 27 | 0.1 | 692 | 510 | 315 | 195 | 118 | 6.7 | 10.7 | 128 | 842 | 152
2019-12-16 | 8.05 | 30 | 0.2 | 700 | 525 | 277 | 248 | 111 | 6.7 | 10.7 | 130 | 840 | 152
2019-12-17 | 8 | 29 | 0.2 | 690 | 520 | 270 | 250 | 111 | 6.7 | 10.7 | 128 | 862 | 154
2019-12-18 | 7.92 | 31 | 0.2 | 733 | 550 | 270 | 280 | 118 | 6.8 | 10.8 | 130 | 880 | 158
2019-12-19 | 8.12 | 31 | 0.1 | 709 | 520 | 289 | 231 | 116 | 6.5 | 10.5 | 130 | 845 | 155
2019-12-20 | 7.88 | 29 | 0.2 | 792 | 539 | 302 | 237 | 124 | 6.6 | 10.6 | 130 | 860 | 156
2019-12-21 | 7.7 | 26 | 0.1 | 700 | 529 | 298 | 231 | 119 | 6.5 | 10.5 | 128 | 849 | 150
2019-12-22 | 7.7 | 27 | 0.1 | 692 | 538 | 290 | 248 | 130 | 6.7 | 10.7 | 115 | 860 | 154
2019-12-23 | 7.79 | 28 | 0.1 | 715 | 550 | 310 | 240 | 133 | 6.6 | 10.6 | 118 | 869 | 159
2019-12-24 | 8.15 | 29 | 0.1 | 690 | 496 | 294 | 202 | 138 | 6.9 | 10.9 | 130 | 850 | 145
2019-12-25 | 8.09 | 25 | 0.1 | 720 | 500 | 302 | 198 | 142 | 6.8 | 10.8 | 142 | 840 | 148
2019-12-26 | 8.1 | 24 | 0.1 | 733 | 510 | 310 | 200 | 148 | 6.6 | 10.6 | 130 | 820 | 150
2019-12-27 | 8.24 | 19 | 0.1 | 759 | 548 | 320 | 228 | 135 | 6.3 | 10.3 | 133 | 840 | 145
2019-12-28 | 8.2 | 19 | 0.1 | 763 | 540 | 319 | 221 | 138 | 6.4 | 10.4 | 138 | 829 | 140
2019-12-29 | 8.19 | 20 | 0.1 | 770 | 466 | 294 | 172 | 134 | 6.7 | 10.7 | 130 | 830 | 142
2019-12-30 | 8.1 | 23 | 0.1 | 720 | 490 | 298 | 192 | 138 | 6 | 10 | 130 | 828 | 145
2019-12-31 | 8.13 | 22 | 0.1 | 733 | 498 | 302 | 196 | 138 | 6.2 | 10.2 | 129 | 828 | 146
MIN | 7.6 | 19 | 0.1 | 648 | 441 | 270 | 137 | 104 | 6 | 10 | 115 | 810 | 158
MAX. | 8.24 | 36 | 0.2 | 1087 | 589 | 353 | 280 | 148 | 6.9 | 10.9 | 142 | 880 | 159
AVG. | 7.9565 | 27.7742 | 0.13548 | 741.8065 | 522.3226 | 307.4194 | 213.3103 | 126.7742 | 6.5742 | 10.5774 | 129.4516 | 844.129 | 148.2903
No. of < Spec | 0 | 2 | 31 | 31 | 31 | 31 | 30 | 31 | 0 | 0 | 31 | 31 | 31
No. of > Spec | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
% < Specs. | 0 | 6.4516 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 100
% > Specs. | 0 | 90.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0