## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SULFATE | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | 10 to 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2017-12-01 | 7.93 | 43 | 0.1 | 1490 | 543 | 314 | 229 | 411 | 6.5 | 10.5 | 105 | 690 | 100
2017-12-02 | 8.2 | 40 | 0.2 | 1690 | 528 | 300 | 228 | 404 | 6.8 | 10.8 | 108 | 680 | 104
2017-12-03 | 8.1 | 35 | 0.1 | 1520 | 532 | 302 | 230 | 402 | 6.9 | 10.9 | 106 | 670 | 108
2017-12-04 | 8.01 | 30 | 0.1 | 1430 | 540 | 310 | 230 | 400 | 6.5 | 10.5 | 105 | 660 | 110
2017-12-05 | 8.01 | 23 | 0.1 | 1310 | 514 | 306 | 208 | 389 | 6.6 | 10.6 | 110 | 673 | 110
2017-12-06 | 8.07 | 20 | 0.1 | 1240 | 486 | 282 | 204 | 288 | 7 | 11 | 115 | 640 | 112
2017-12-07 | 8.13 | 18 | 0.1 | 1370 | 481 | 273 | 208 | 303 | 6.5 | 10.5 | 110 | 683 | 120
2017-12-08 | 7.75 | 16 | 0.1 | 1530 | 551 | 326 | 225 | 346 | 6.8 | 10.8 | 114 | 643 | 105
2017-12-09 | 7.6 | 18 | 0.1 | 1640 | 640 | 350 | 290 | 370 | 6.9 | 10.9 | 110 | 679 | 110
2017-12-10 | 7.8 | 16 | 0.1 | 1740 | 660 | 365 | 295 | 374 | 6.9 | 10.9 | 110 | 674 | 112
2017-12-11 | 7.9 | 17 | 0.1 | 1780 | 682 | 372 | 310 | 400 | 6.8 | 10.8 | 100 | 670 | 112
2017-12-12 | 7.92 | 19 | 0.1 | 1890 | 689 | 360 | 329 | 412 | 6.9 | 10.9 | 110 | 672 | 113
2017-12-13 | 8.02 | 17 | 0.1 | 1920 | 554 | 326 | 228 | 407 | 6.8 | 10.8 | 105 | 669 | 110
2017-12-14 | 8.12 | 18 | 0.1 | 1906 | 612 | 448 | 164 | 549 | 6.9 | 10.9 | 110 | 682 | 113
2017-12-15 | 8.01 | 19 | 0.1 | 1896 | 685 | 396 | 289 | 542 | 6.6 | 10.6 | 100 | 653 | 103
2017-12-16 | 8.13 | 18 | 0.1 | 1860 | 641 | 384 | 257 | 521 | 6.9 | 10.9 | 109 | 650 | 109
2017-12-17 | 8 | 17 | 0.1 | 1890 | 680 | 392 | 288 | 520 | 6.9 | 10.9 | 100 | 670 | 110
2017-12-18 | 7.64 | 18 | 0.1 | 2012 | 710 | 402 | 308 | 490 | 6.7 | 10.7 | 102 | 687 | 110
2017-12-19 | 7.69 | 18 | 0.1 | 2060 | 714 | 416 | 298 | 521 | 6.8 | 10.8 | 109 | 682 | 107
2017-12-20 | 7.8 | 18 | 0.1 | 2074 | 724 | 390 | 334 | 540 | 6.6 | 10.6 | 110 | 693 | 110
2017-12-21 | 7.56 | 16 | 0.1 | 2096 | 730 | 392 | 338 | 542 | 6.7 | 10.7 | 100 | 690 | 115
2017-12-22 | 7.52 | 16 | 0.1 | 2160 | 714 | 388 | 326 | 528 | 6.5 | 10.5 | 109 | 684 | 118
2017-12-23 | 7.53 | 18 | 0.1 | 2219 | 809 | 445 | 364 | 542 | 6.7 | 10.7 | 104 | 720 | 120
2017-12-24 | 7.65 | 17 | 0.1 | 2170 | 780 | 425 | 355 | 525 | 6.8 | 10.8 | 110 | 728 | 122
2017-12-25 | 7.64 | 16 | 0.2 | 1980 | 730 | 404 | 326 | 499 | 6.8 | 10.8 | 116 | 732 | 124
2017-12-26 | 7.92 | 18 | 0.1 | 2393 | 785 | 470 | 315 | 507 | 6.7 | 10.7 | 120 | 738 | 117
2017-12-27 | 7.49 | 18 | 0.1 | 2480 | 777 | 479 | 298 | 492 | 6.7 | 10.7 | 104 | 732 | 139
2017-12-28 | 7.7 | 16 | 0.1 | 2360 | 907 | 538 | 369 | 499 | 6.7 | 10.7 | 107 | 694 | 125
2017-12-29 | 8.12 | 16 | 0.1 | 2190 | 794 | 458 | 336 | 521 | 6.5 | 10.5 | 115 | 673 | 120
2017-12-30 | 8.02 | 18 | 0.2 | 1790 | 692 | 402 | 290 | 420 | 6.7 | 10.7 | 110 | 680 | 129
2017-12-31 | 7.98 | 17 | 0.1 | 1750 | 680 | 396 | 284 | 418 | 6.6 | 10.6 | 110 | 675 | 125
MIN. | 7.49 | 16 | 0.1 | 1240 | 481 | 273 | 164 | 288 | 6.5 | 10.5 | 100 | 640 | 100
MAX. | 8.2 | 43 | 0.2 | 2480 | 907 | 538 | 369 | 549 | 7 | 11 | 120 | 738 | 139
AVG. | 7.8697 | 20.129 | 0.10968 | 1865.6774 | 663.3548 | 381 | 284.1333 | 454.2581 | 6.7323 | 10.7323 | 108.1613 | 682.7742 | 114.2581
No. of < Spec | 1 | -- | 26 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 10 | 5 | 0 | 6 | 0 | -- | -- | 11 | 0 | 0 | - | 0 | 0
% < Specs. | 3.5714 | -- | 92.8571 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 35.7143 | 17.8571 | 0 | 21.4286 | 0 | - | -- | 39.2857 | 0 | 0 | - | 0 | 0