## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | Total PO4 | T. Alk. | Total Iron | Sulphate | SiO2
| 7.2-8.2 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | Max. 2 ppm | Max. 1000 ppm | 180 ppm
2018-03-01 | 7.38 | 16 | 0.1 | 1825 | 1151 | 608 | 543 | 267 | 4 | 102 | 0.2 | 982 | 159
2018-03-02 | 7.4 | 14 | 0.1 | 1809 | 1138 | 600 | 538 | 265 | 4 | 104 | 0.2 | 980 | 158
2018-03-03 | 7.2 | 18 | 0.1 | 1832 | 1179 | 653 | 526 | 317 | 4 | 100 | 0.2 | 963 | 155
2018-03-04 | 7.43 | 17 | 0.2 | 1804 | 1160 | 645 | 515 | 315 | 4 | 102 | 0.2 | 963 | 154
2018-03-05 | 7.62 | 18 | 0.1 | 1763 | 1084 | 580 | 504 | 250 | 4 | 100 | 0.2 | 989 | 153
2018-03-06 | 7.5 | 14 | 0.2 | 1740 | 1080 | 576 | 504 | 247 | 4.2 | 102 | 0.2 | 980 | 159
2018-03-07 | 7.53 | 18 | 0.1 | 1750 | 1030 | 540 | 490 | 250 | 4 | 103 | 0.2 | 972 | 159
2018-03-08 | 7.6 | 15 | 0.1 | 1720 | 1070 | 559 | 511 | 267 | 4 | 110 | 0.2 | 969 | 158
2018-03-09 | 7.54 | 15 | 0.2 | 1673 | 1061 | 551 | 510 | 259 | 4 | 106 | 0.2 | 960 | 148
2018-03-10 | 7.38 | 18 | 0.2 | 1650 | 1040 | 540 | 500 | 252 | 4.1 | 100 | 0.2 | 964 | 173
2018-03-11 | 7.29 | 17 | 0.1 | 1673 | 1053 | 543 | 510 | 250 | 4 | 102 | 0.2 | 962 | 172
2018-03-12 | 7.4 | 14 | 0.2 | 1830 | 1049 | 563 | 486 | 257 | 4 | 104 | 0.2 | 984 | 164
2018-03-13 | 7.48 | 14 | 0.2 | 1620 | 1016 | 551 | 465 | 252 | 4 | 100 | 0.2 | 982 | 155
2018-03-14 | 7.3 | 15 | 0.2 | 1843 | 1053 | 567 | 486 | 274 | 4 | 103 | 0.2 | 994 | 148
2018-03-15 | 7.48 | 16 | 0.2 | 2080 | 1239 | 670 | 569 | 329 | 4 | 100 | 0.2 | 998 | 163
2018-03-16 | 7.53 | 19 | 0.1 | 2214 | 1354 | 710 | 644 | 335 | 4 | 102 | 0.2 | 1010 | 179
2018-03-17 | 7.4 | 19 | 0.1 | 2083 | 1293 | 680 | 613 | 310 | 4 | 100 | 0.2 | 1033 | 205
2018-03-18 | 7.48 | 17 | 0.1 | 2120 | 1326 | 685 | 641 | 317 | 4.1 | 102 | 0.2 | 1031 | 204
2018-03-19 | 7.29 | 20 | 0.1 | 2091 | 1265 | 690 | 575 | 288 | 4 | 103 | 0.2 | 1040 | 216
2018-03-20 | 7.56 | 19 | 0.1 | 1823 | 1200 | 602 | 598 | 315 | 4 | 102 | 0.2 | 1020 | 230
2018-03-21 | 7.46 | 17 | 0.2 | 1860 | 1173 | 600 | 573 | 306 | 4 | 117 | 0.2 | 1004 | 230
2018-03-22 | 7.58 | 15 | 0.1 | 1720 | 1090 | 568 | 522 | 300 | 4 | 114 | 0.2 | 993 | 239
2018-03-23 | 7.38 | 15 | 0.2 | 1695 | 1098 | 570 | 528 | 288 | 4 | 120 | 0.2 | 985 | 224
2018-03-24 | 7.3 | 13 | 0.5 | 1610 | 1024 | 536 | 488 | 281 | 4 | 112 | 0.2 | 982 | 225
2018-03-25 | 7.39 | 14 | 0.1 | 1592 | 1010 | 530 | 480 | 282 | 4 | 115 | 0.2 | 980 | 215
2018-03-26 | 7.62 | 16 | 0.3 | 1622 | 1033 | 543 | 490 | 280 | 4 | 118 | 0.2 | 1012 | 210
2018-03-27 | 7.28 | 20 | 0.2 | 1632 | 1036 | 552 | 484 | 274 | 4 | 110 | 0.2 | 970 | 213
2018-03-28 | 7.53 | 18 | 0.1 | 1689 | 1024 | 548 | 476 | 267 | 4.1 | 118 | 0.2 | 982 | 214
2018-03-29 | 7.48 | 17 | 0.1 | 1660 | 1013 | 540 | 473 | 265 | 4 | 119 | 0.2 | 980 | 210
2018-03-30 | 7.62 | 16 | 0.1 | 1640 | 1000 | 535 | 465 | 260 | 4 | 115 | 0.2 | 978 | 193
2018-03-31 | 7.67 | 13 | 0.1 | 1583 | 973 | 540 | 433 | 253 | 4 | 113 | 0.2 | 969 | 183
MIN. | 7.2 | 13 | 0.1 | 1583 | 973 | 530 | 433 | 247 | 4 | 100 | 0.2 | 960 | 148
MAX. | 7.67 | 20 | 0.5 | 2214 | 1354 | 710 | 644 | 335 | 4.2 | 120 | 0.2 | 1040 | 239
AVG. | 7.4548 | 16.3548 | 0.15484 | 1782.129 | 1106.9355 | 586.2903 | 519.9 | 279.7419 | 4.0161 | 107.0323 | 0.2 | 987.4516 | 186.0645
No. of < Spec | 0 | -- | 18 | -- | -- | -- | -- | -- | 0 | -- | -- | -- | --
No. of > Spec | 0 | 0 | 0 | 2 | 29 | 1 | -- | 0 | 0 | 0 | 0 | 7 | 15
% < Specs. | 0 | -- | 58.0645 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 0 | 0 | 6.4516 | 93.5484 |  | -- | 0 | 0 | 0 | 0 | 22.5806 | 48.3871
No. of < Spec | 19 | -- | 17 | -- | -- | -- | -- | -- | 1 | -- | -- | -- | --
No. of > Spec | 0 | 0 | 1 | 3 | 28 | 2 | -- | 0 | 0 | 0 | 0 | 31 | 17
% < Specs. | 59.375 | -- | 53.125 | -- | -- | -- | -- | -- | 3.125 | - | - | - | --
% > Specs. | 0 | 0 | 3.125 | 9.6774 | 90.3226 | 0 | -- | 0 | 0 | 0 | 0 | 100 | 54.8387