## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | Total PO4 | T. Alk. | Total Iron | Sulphate | SiO2
| 7.2-8.2 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | Max. 2 ppm | Max. 1000 ppm | 180 ppm
2018-03-01 | 7.62 | 37 | 0.1 | 1716 | 1012 | 567 | 445 | 252 | 4 | 108 | 0.2 | 970 | 158
2018-03-02 | 7.5 | 34 | 0.1 | 1702 | 1002 | 560 | 442 | 282 | 4 | 106 | 0.2 | 972 | 160
2018-03-03 | 7.54 | 49 | 0.1 | 1593 | 918 | 526 | 392 | 303 | 4 | 104 | 0.2 | 970 | 158
2018-03-04 | 7.42 | 48 | 0.1 | 1573 | 903 | 520 | 383 | 305 | 4 | 102 | 0.2 | 968 | 169
2018-03-05 | 7.34 | 50 | 0.1 | 1653 | 938 | 508 | 430 | 238 | 4 | 102 | 0.2 | 992 | 166
2018-03-06 | 7.28 | 52 | 0.1 | 1520 | 910 | 490 | 420 | 236 | 4 | 102 | 0.2 | 990 | 164
2018-03-07 | 7.48 | 59 | 0.1 | 1486 | 902 | 486 | 416 | 245 | 4 | 110 | 0.2 | 984 | 170
2018-03-08 | 7.39 | 52 | 0.1 | 1573 | 910 | 490 | 420 | 274 | 4 | 115 | 0.2 | 974 | 169
2018-03-09 | 7.68 | 48 | 0.1 | 1533 | 918 | 502 | 416 | 281 | 4 | 109 | 0.2 | 975 | 156
2018-03-10 | 7.9 | 58 | 0.1 | 1580 | 934 | 514 | 420 | 288 | 4 | 110 | 0.2 | 994 | 169
2018-03-11 | 7.82 | 62 | 0.1 | 1842 | 1044 | 551 | 493 | 278 | 4 | 108 | 0.2 | 998 | 162
2018-03-12 | 7.78 | 60 | 0.1 | 1829 | 1020 | 548 | 472 | 274 | 4 | 100 | 0.2 | 996 | 159
2018-03-13 | 7.62 | 59 | 0.1 | 1653 | 1084 | 580 | 504 | 288 | 4 | 102 | 0.2 | 990 | 162
MIN. | 7.28 | 34 | 0.1 | 1486 | 902 | 486 | 383 | 236 | 4 | 100 | 0.2 | 968 | 156
MAX. | 7.9 | 62 | 0.1 | 1842 | 1084 | 580 | 504 | 305 | 4 | 115 | 0.2 | 998 | 170
AVG. | 7.5669 | 51.3846 | 0.1 | 1634.8462 | 961.1538 | 526.3077 | 434.8462 | 272.6154 | 4 | 106 | 0.2 | 982.5385 | 163.2308
No. of < Spec | 0 | -- | 13 | -- | -- | -- | -- | -- | 0 | -- | -- | -- | --
No. of > Spec | 0 | 13 | 0 | 0 | 5 | 0 | -- | 0 | 0 | 0 | 0 | 0 | 0
% < Specs. | 0 | -- | 100 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 100 | 0 | 0 | 38.4615 |  | -- | 0 | 0 | 0 | 0 | 0 | 0
No. of < Spec | 7 | -- | 13 | -- | -- | -- | -- | -- | 1 | -- | -- | -- | --
No. of > Spec | 0 | 13 | 1 | 0 | 4 | 0 | -- | 0 | 0 | 0 | 0 | 13 | 0
% < Specs. | 50 | -- | 92.8571 | -- | -- | -- | -- | -- | 7.1429 | - | - | - | --
% > Specs. | 0 | 100 | 7.1429 | 0 | 30.7692 | 0 | -- | 0 | 0 | 0 | 0 | 100 | 0