## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SULFATE | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1000 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | 10 to 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2017-02-01 | 7.7 | 20 | 0.8 | 1070 | 244 | 148 | 96 | 314 | 6.8 | 10.8 | 100 | 334 | 60
2017-02-02 | 7.67 | 24 | 0.2 | 1030 | 252 | 156 | 96 | 307 | 6.9 | 10.9 | 100 | 320 | 60
2017-02-03 | 7.65 | 15 | 0.1 | 920 | 248 | 148 | 100 | 300 | 6.9 | 10.9 | 100 | 315 | 65
2017-02-04 | 7.7 | 19 | 0.2 | 985 | 256 | 156 | 100 | 307 | 6.8 | 10.8 | 100 | 348 | 63
2017-02-05 | 7.67 | 22 | 0.1 | 990 | 260 | 168 | 92 | 295 | 6.5 | 10.5 | 100 | 360 | 65
2017-02-06 | 7.57 | 27 | 0 | 910 | 248 | 152 | 96 | 300 | 6.9 | 10.9 | 100 | 340 | 64
2017-02-07 | 7.4 | 16 | 0 | 994 | 252 | 160 | 92 | 307 | 6.5 | 10.5 | 100 | 324 | 67
2017-02-08 | 7.52 | 15 | 0.2 | 1065 | 256 | 164 | 92 | 314 | 6.7 | 10.7 | 100 | 362 | 65
2017-02-09 | 7.5 | 28 | 0.1 | 950 | 252 | 164 | 88 | 293 | 6.9 | 10.9 | 100 | 360 | 68
2017-02-10 | 7.6 | 20 | 0.1 | 1100 | 256 | 156 | 100 | 278 | 6.6 | 10.6 | 100 | 355 | 65
2017-02-11 | 7.49 | 24 | 0.2 | 940 | 260 | 168 | 92 | 285 | 6.5 | 10.5 | 100 | 368 | 69
2017-02-12 | 7.65 | 23 | 0 | 960 | 248 | 148 | 100 | 280 | 6.3 | 10.3 | 100 | 350 | 66
2017-02-13 | 7.93 | 24 | 0 | 950 | 256 | 160 | 96 | 278 | 6.8 | 10.8 | 100 | 360 | 70
2017-02-14 | 7.64 | 16 | 0 | 1080 | 264 | 168 | 96 | 227 | 6.7 | 10.7 | 100 | 365 | 68
2017-02-15 | 7.23 | 22 | 1 | 1152 | 244 | 152 | 92 | 241 | 6.8 | 10.8 | 102 | 366 | 70
2017-02-16 | 7.54 | 31 | 0 | 1100 | 240 | 148 | 92 | 234 | 6.6 | 10.6 | 100 | 365 | 66
2017-02-17 | 7.75 | 30 | 0.1 | 1110 | 256 | 162 | 94 | 238 | 6.8 | 10.8 | 100 | 344 | 65
2017-02-18 | 7.54 | 26 | 0.2 | 1090 | 264 | 172 | 92 | 234 | 6.5 | 105 | 100 | 360 | 64
2017-02-19 | 7.45 | 24 | 0.2 | 1050 | 260 | 156 | 104 | 235 | 6.6 | 10.6 | 100 | 350 | 65
2017-02-20 | 7.37 | 27 | 0 | 1090 | 240 | 156 | 84 | 241 | 6.8 | 10.8 | 100 | 355 | 60
2017-02-21 | 7.47 | 30 | 0 | 1040 | 248 | 169 | 79 | 249 | 6.9 | 10.9 | 100 | 350 | 69
2017-02-22 | 7.49 | 34 | 0.3 | 980 | 256 | 164 | 92 | 293 | 6.7 | 10.7 | 100 | 328 | 67
2017-02-23 | 7.4 | 38 | 0 | 970 | 252 | 160 | 92 | 227 | 6.9 | 10.9 | 100 | 340 | 62
2017-02-24 | 7.5 | 22 | 0.2 | 995 | 265 | 173 | 92 | 254 | 6.5 | 10.5 | 100 | 360 | 64
2017-02-25 | 7.39 | 48 | 0.5 | 972 | 260 | 176 | 84 | 241 | 6.6 | 10.6 | 100 | 368 | 61
2017-02-26 | 7.7 | 20 | 0.1 | 1110 | 265 | 173 | 92 | 254 | 6.5 | 10.5 | 102 | 362 | 64
2017-02-27 | 7.27 | 22 | 0.2 | 1045 | 264 | 172 | 92 | 249 | 6.6 | 10.6 | 100 | 360 | 65
2017-02-28 | 7.9 | 39 | 0 | 1120 | 268 | 172 | 96 | 256 | 6.7 | 10.7 | 100 | 366 | 63
MIN. | 7.23 | 15 | 0 | 910 | 240 | 148 | 79 | 227 | 6.3 | 10.3 | 100 | 315 | 60
MAX. | 7.93 | 48 | 1 | 1152 | 268 | 176 | 104 | 314 | 6.9 | 105 | 102 | 368 | 70
AVG. | 7.5604 | 25.2143 | 0.17143 | 1027.4286 | 254.7857 | 161.4643 | 93.3214 | 268.9643 | 6.6893 | 14.0643 | 100.1429 | 351.25 | 65
No. of < Spec | 10 | -- | 16 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 20 | 2 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 35.7143 | -- | 57.1429 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 71.4286 | 7.1429 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0