## Sheet1
CIRCULATING WATER ANALYSIS FOR X 01 COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SO4-2 | SiO2
| 7.5-8.3 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2018-04-01 | 7.9 | 18 | 0.1 | 1587 | 980 | 513 | 467 | 326 | 6.5 | 10.5 | 118 | 770 | 140
2018-04-02 | 7.93 | 17 | 0.1 | 1493 | 924 | 508 | 416 | 324 | 6.5 | 10.5 | 119 | 772 | 138
2018-04-03 | 8 | 18 | 0.1 | 1548 | 939 | 523 | 416 | 338 | 6.5 | 10.5 | 116 | 774 | 153
2018-04-04 | 7.83 | 14 | 0.1 | 1450 | 912 | 492 | 420 | 331 | 6.5 | 10.5 | 119 | 722 | 140
2018-04-05 | 8 | 17 | 0.1 | 1325 | 729 | 389 | 340 | 288 | 6.8 | 10.8 | 114 | 738 | 137
2018-04-06 | 7.96 | 18 | 0.1 | 1290 | 680 | 360 | 320 | 267 | 6.7 | 10.7 | 117 | 730 | 130
2018-04-07 | 8.09 | 18 | 0.1 | 1165 | 624 | 328 | 296 | 259 | 6.5 | 10.5 | 120 | 728 | 132
2018-04-08 | 8.1 | 17 | 0.1 | 1184 | 640 | 339 | 301 | 259 | 6.6 | 10.6 | 120 | 728 | 130
2018-04-09 | 7.92 | 14 | 0.1 | 1140 | 650 | 342 | 308 | 245 | 6.8 | 10.8 | 123 | 760 | 148
2018-04-10 | 7.82 | 15 | 0.1 | 1080 | 620 | 320 | 300 | 228 | 6.7 | 10.7 | 124 | 750 | 142
2018-04-11 | 7.69 | 16 | 0.1 | 984 | 537 | 312 | 225 | 210 | 6.8 | 10.8 | 120 | 733 | 138
2018-04-12 | 7.7 | 16 | 0.1 | 993 | 480 | 272 | 208 | 181 | 7 | 10 | 110 | 720 | 138
2018-04-13 | 7.73 | 15 | 0.1 | 1020 | 495 | 279 | 216 | 183 | 7 | 10 | 112 | 722 | 139
2018-04-14 | 7.36 | 15 | 0.1 | 884 | 524 | 287 | 237 | 188 | 6.8 | 10.8 | 114 | 718 | 130
2018-04-15 | 7.42 | 14 | 0.1 | 899 | 533 | 293 | 240 | 186 | 6.8 | 10.8 | 114 | 716 | 128
2018-04-16 | 7.69 | 16 | 0.1 | 984 | 537 | 312 | 225 | 210 | 6.8 | 10.8 | 120 | 733 | 138
2018-04-17 | 7.8 | 16 | 0.1 | 998 | 568 | 324 | 244 | 220 | 6.9 | 10.9 | 118 | 693 | 140
2018-04-18 | 8.1 | 17 | 0.1 | 1092 | 590 | 410 | 180 | 210 | 6.7 | 10.7 | 120 | 689 | 142
2018-04-19 | 7.78 | 17 | 0.1 | 1070 | 591 | 316 | 275 | 217 | 6.7 | 10.7 | 118 | 690 | 128
2018-04-20 | 7.91 | 16 | 0.1 | 1137 | 624 | 341 | 283 | 232 | 6.7 | 10.7 | 114 | 685 | 125
2018-04-21 | 8.02 | 14 | 0.1 | 1160 | 616 | 358 | 258 | 225 | 6.9 | 10.9 | 119 | 730 | 137
2018-04-22 | 8 | 16 | 0.1 | 1152 | 610 | 355 | 255 | 224 | 6.9 | 10.9 | 118 | 728 | 135
2018-04-23 | 7.76 | 18 | 0.1 | 1265 | 695 | 349 | 346 | 253 | 6.9 | 10.9 | 114 | 720 | 139
2018-04-24 | 7.83 | 19 | 0.1 | 1290 | 699 | 359 | 340 | 258 | 6.7 | 10.7 | 125 | 742 | 140
2018-04-25 | 8.1 | 19 | 0.1 | 1240 | 703 | 374 | 329 | 246 | 6.7 | 10.7 | 125 | 714 | 132
2018-04-26 | 7.7 | 18 | 0.1 | 1302 | 740 | 374 | 366 | 246 | 6.9 | 10.9 | 116 | 722 | 142
2018-04-27 | 7.67 | 18 | 0.1 | 1315 | 761 | 412 | 349 | 267 | 6.9 | 10.9 | 116 | 743 | 136
2018-04-28 | 8.01 | 15 | 0.2 | 1320 | 770 | 420 | 350 | 282 | 7 | 11 | 120 | 748 | 130
2018-04-29 | 7.88 | 14 | 0.2 | 1343 | 784 | 443 | 341 | 284 | 6.9 | 10.9 | 118 | 746 | 129
2018-04-30 | 7.82 | 15 | 0.1 | 1360 | 790 | 450 | 340 | 286 | 7 | 11 | 118 | 752 | 130
MIN | 7.36 | 14 | 0.1 | 884 | 480 | 272 | 180 | 181 | 6.5 | 10 | 110 | 685 | 125
MAX. | 8.1 | 19 | 0.2 | 1587 | 980 | 523 | 420 | 338 | 7 | 11 | 125 | 774 | 153
AVG. | 7.8507 | 16.3333 | 0.10667 | 1202.3333 | 678.1667 | 371.8 | 296.7143 | 249.1 | 6.77 | 10.7033 | 117.9667 | 730.5333 | 136.2
No. of < Spec | 2 | -- | 28 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 0 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 6.6667 | -- | 93.3333 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 0 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0