## Sheet1
CIRCULATING WATER ANALYSIS FOR X 01 COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SO4-2 | SiO2
| 7.5-8.3 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2017-03-01 | 7.8 | 24 | 0.1 | 1340 | 800 | 512 | 288 | 212 | 6.4 | 10.4 | 115 | 764 | 130
2017-03-02 | 7.85 | 21 | 0.1 | 1338 | 793 | 470 | 323 | 205 | 6.3 | 10.3 | 110 | 752 | 129
2017-03-03 | 8.1 | 17 | 0.1 | 1237 | 810 | 500 | 310 | 212 | 6.2 | 10.2 | 110 | 750 | 120
2017-03-04 | 7.9 | 20 | NIL | 1327 | 810 | 498 | 312 | 219 | 6.3 | 10.3 | 110 | 756 | 120
2017-03-05 | 7.87 | 18 | NIL | 1342 | 834 | 510 | 324 | 220 | 6.2 | 10.2 | 107 | 740 | 124
2017-03-06 | 7.6 | 22 | 0.1 | 1292 | 824 | 408 | 416 | 212 | 6 | 10 | 110 | 750 | 130
2017-03-07 | 7.84 | 17 | NIL | 1370 | 818 | 521 | 297 | 234 | 6 | 10 | 110 | 760 | 128
2017-03-08 | 8 | 18 | NIL | 1540 | 824 | 508 | 316 | 219 | 6.1 | 10.1 | 104 | 752 | 122
2017-03-09 | 7.9 | 17 | NIL | 1692 | 1062 | 639 | 423 | 307 | 6.2 | 10.2 | 104 | 740 | 120
2017-03-10 | 8.13 | 15 | NIL | 1787 | 1092 | 660 | 432 | 314 | 6.5 | 10.5 | 107 | 760 | 129
2017-03-11 | 7.96 | 20 | NIL | 1789 | 1131 | 669 | 462 | 322 | 6.4 | 10.4 | 103 | 745 | 122
2017-03-12 | 8 | 20 | 0.1 | 1502 | 756 | 429 | 327 | 216 | 6.3 | 10.3 | 116 | 786 | 138
2017-03-13 | 8.2 | 24 | 0.2 | 1492 | 779 | 480 | 299 | 227 | 6.2 | 10.2 | 112 | 780 | 145
2017-03-14 | 8.09 | 16 | 0.1 | 1721 | 1068 | 636 | 432 | 307 | 6.2 | 10.2 | 100 | 760 | 124
2017-03-15 | 8.1 | 19 | NIL | 1620 | 794 | 450 | 344 | 234 | 6.2 | 10.2 | 114 | 782 | 145
2017-03-16 | 8.1 | 17 | NIL | 1671 | 1098 | 640 | 458 | 314 | 6.3 | 10.3 | 104 | 750 | 122
2017-03-17 | 8.03 | 17 | NIL | 1772 | 1032 | 630 | 402 | 307 | 6 | 10 | 112 | 760 | 125
2017-03-18 | 7.93 | 16 | NIL | 1760 | 1026 | 620 | 406 | 300 | 6.1 | 10.1 | 114 | 750 | 135
2017-03-19 | 7.8 | 17 | NIL | 1690 | 1010 | 612 | 398 | 297 | 6 | 10 | 110 | 765 | 134
2017-03-20 | 8.12 | 14 | NIL | 1690 | 1022 | 630 | 392 | 295 | 6.1 | 10.1 | 114 | 760 | 130
2017-03-21 | 7.92 | 14 | NIL | 1650 | 1029 | 627 | 402 | 290 | 6.2 | 10.2 | 112 | 750 | 134
2017-03-22 | 8 | 20 | NIL | 1610 | 1076 | 692 | 384 | 263 | 6 | 10 | 114 | 765 | 130
2017-03-23 | 7.85 | 17 | 0.1 | 1480 | 970 | 635 | 335 | 260 | 6.3 | 10.3 | 112 | 760 | 134
2017-03-24 | 7.74 | 15 | 0.1 | 1597 | 992 | 664 | 328 | 249 | 6.4 | 10.4 | 104 | 750 | 135
2017-03-25 | 7.7 | 16 | NIL | 1582 | 990 | 670 | 320 | 248 | 6.3 | 10.3 | 105 | 760 | 137
2017-03-26 | 7.69 | 15 | NIL | 1620 | 971 | 652 | 319 | 252 | 6.2 | 10.2 | 104 | 740 | 130
2017-03-27 | 8.13 | 24 | 0.1 | 1342 | 938 | 579 | 359 | 241 | 6 | 10 | 114 | 765 | 140
2017-03-28 | 7.6 | 16 | 0.1 | 1289 | 896 | 496 | 400 | 249 | 6.2 | 10.2 | 110 | 760 | 142
2017-03-29 | 7.82 | 15 | NIL | 1192 | 910 | 580 | 330 | 252 | 6.3 | 10.3 | 110 | 765 | 140
2017-03-30 | 7.89 | 17 | NIL | 1264 | 876 | 552 | 324 | 227 | 6.4 | 10.4 | 109 | 750 | 138
2017-03-31 | 7.67 | 14 | NIL | 1290 | 858 | 551 | 307 | 219 | 6.2 | 10.2 | 109 | 740 | 130
MIN | 7.6 | 14 | 0.1 | 1192 | 756 | 408 | 288 | 205 | 6 | 10 | 100 | 740 | 120
MAX. | 8.2 | 24 | 0.2 | 1789 | 1131 | 692 | 462 | 322 | 6.5 | 10.5 | 116 | 786 | 145
AVG. | 7.9139 | 17.8065 | 0.10909 | 1512.5161 | 931.9032 | 571.6129 | 360.2903 | 255.5806 | 6.2097 | 10.2097 | 109.3226 | 757 | 131.0323
No. of < Spec | 0 | -- | 10 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 0 | 5 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 0 | -- | 90.9091 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 17.8571 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | 0