## Sheet1
CIRCULATING WATER ANALYSIS FOR X 01 COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | SO4-2 | SiO2
| 7.5 - 8.3 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 12 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm
2018-09-01 | 7.79 | 22 | 0.1 | 693 | 331 | 208 | 123 | 219 | 6.6 | 10.6 | 123 | 587 | 154
2018-09-02 | 7.8603 | 20 | 0.1 | 712 | 345 | 215 | 130 | 220 | 6.6 | 10.6 | 125 | 572 | 152
2018-09-03 | 8.18 | 17 | 0.2 | 670 | 340 | 238 | 102 | 156 | 6.7 | 10.7 | 126 | 540 | 142
2018-09-04 | 8.2 | 16 | 0.1 | 640 | 323 | 210 | 113 | 146 | 6.7 | 10.7 | 126 | 533 | 144
2018-09-05 | 8.09 | 15 | 0.1 | 536 | 310 | 189 | 121 | 124 | 6.8 | 10.8 | 123 | 508 | 147
2018-09-06 | 8 | 16 | 0.1 | 550 | 400 | 243 | 157 | 174 | 6.9 | 10.9 | 124 | 550 | 150
2018-09-07 | 8.4 | 18 | 0.1 | 491 | 336 | 181 | 155 | 161 | 6.6 | 10.6 | 129 | 480 | 161
2018-09-08 | 8.38 | 18 | 0.1 | 490 | 344 | 185 | 159 | 168 | 6.9 | 10.9 | 119 | 473 | 149
2018-09-09 | 7.89 | 15 | 0.1 | 643 | 338 | 210 | 128 | 153 | 6.9 | 10.9 | 120 | 595 | 145
2018-09-10 | 7.93 | 16 | 0.1 | 664 | 359 | 219 | 140 | 154 | 6.9 | 10.9 | 120 | 593 | 148
2018-09-11 | 7.82 | 14 | 0.1 | 621 | 320 | 206 | 114 | 146 | 6.7 | 10.7 | 118 | 434 | 147
2018-09-12 | 8.02 | 16 | 0.2 | 625 | 334 | 182 | 152 | 159 | 6.6 | 10.6 | 120 | 398 | 140
2018-09-13 | 7.7 | 16 | 0.2 | 689 | 380 | 228 | 152 | 180 | 7 | 11 | 118 | 610 | 153
2018-09-14 | 7.66 | 16 | 0.2 | 673 | 365 | 200 | 165 | 181 | 7 | 11 | 120 | 370 | 150
2018-09-15 | 7.76 | 16 | 0.1 | 774 | 420 | 238 | 182 | 203 | 6.7 | 10.7 | 110 | 398 | 152
2018-09-16 | 7.95 | 15 | 0.1 | 751 | 433 | 244 | 189 | 204 | 6.6 | 10.6 | 112 | 402 | 150
2018-09-17 | 8.2 | 19 | 0.1 | 740 | 402 | 213 | 189 | 166 | 6.5 | 10.5 | 130 | 370 | 149
2018-09-18 | 8.38 | 19 | 0.1 | 748 | 418 | 220 | 198 | 169 | 6.7 | 10.7 | 132 | 347 | 150
2018-09-19 | 8.32 | 19 | 0.1 | 740 | 410 | 220 | 190 | 231 | 6.9 | 10.9 | 138 | 392 | 146
2018-09-20 | 8.2 | 20 | 0.1 | 699 | 418 | 234 | 184 | 225 | 6.9 | 10.9 | 124 | 689 | 150
2018-09-21 | 8.38 | 18 | 0.1 | 740 | 460 | 260 | 200 | 164 | 6.7 | 10.7 | 133 | 513 | 154
2018-09-22 | 8.49 | 15 | 0.1 | 776 | 428 | 244 | 184 | 152 | 6.8 | 10.8 | 134 | 530 | 142
2018-09-23 | 8.4 | 14 | 0.1 | 789 | 449 | 253 | 196 | 153 | 6.8 | 10.8 | 134 | 532 | 140
2018-09-24 | 8.12 | 15 | 0.1 | 813 | 463 | 310 | 153 | 158 | 6.6 | 10.6 | 129 | 490 | 146
2018-09-25 | 7.93 | 14 | 0.1 | 742 | 432 | 251 | 181 | 145 | 6.8 | 10.8 | 126 | 380 | 145
2018-09-26 | 7.89 | 17 | 0.1 | 898 | 458 | 265 | 193 | 153 | 6.7 | 10.7 | 124 | 424 | 150
2018-09-27 | 8.08 | 28 | 0.1 | 1050 | 454 | 268 | 186 | 261 | 7 | 11 | 127 | 583 | 158
2018-09-28 | 8.09 | 25 | 0.1 | 1080 | 460 | 290 | 170 | 270 | 7 | 11 | 130 | 596 | 155
2018-09-29 | 7.7 | 24 | 0.1 | 1150 | 488 | 298 | 190 | 276 | 6.9 | 10.9 | 120 | 684 | 158
2018-09-30 | 7.78 | 23 | 0.1 | 1173 | 499 | 309 | 190 | 277 | 6.9 | 10.9 | 120 | 682 | 156
MIN | 7.66 | 14 | 0.1 | 490 | 310 | 181 | 102 | 124 | 6.5 | 10.5 | 110 | 347 | 140
MAX. | 8.49 | 28 | 0.2 | 1173 | 499 | 310 | 200 | 277 | 7 | 11 | 138 | 689 | 161
AVG. | 8.053 | 17.8667 | 0.11333 | 745.3333 | 397.2333 | 234.3667 | 165.4643 | 184.9333 | 6.78 | 10.78 | 124.4667 | 508.5 | 149.4333
No. of < Spec | 0 | 23 | 30 | 30 | 30 | 30 | 29 | 30 | 0 | 0 | 30 | 30 | 30
No. of > Spec | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
% < Specs. | 0 | 76.6667 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 100
% > Specs. | 23.3333 | 16.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0