## Table 1
Wex Tech July - 2013
COOLING WATER TREATMENT
DCM SRIRAM LIMITED
MONTHLY REPORT
REPORT OF COOLING TOWER
DATE : 04/08/2013 Sriram Chemical Ltd., Jagadia, Ankleshwar Gujarat
Kind Attn : Sh. K. R. Vaidya (Unit Head) Subject : Cooling Water Treatment Monthly Report
Dear Sir, Please find enclosed herewith the CWT Monthly Report for your
Cooling water system for the Month of July-13
The report is based on the laboratory analysis done by our representative in presence of your laboratory in charge and data collected from the Control Room. If you need any clarification, please feel free to contact us.
Assuring you of our best services at all times. Thanking you, Yours sincerely, FOR WEX TECHNOLOGIES PVT. LTD.
Vipul Govekar Regional Manager Encl. : a/a C.C. : MR. S. K. TAYAL MR. NAVIN JAISWAL MR. ATUL CHOKSI
EXECUTIVE SUMMARY 1] EXCEPTIONS CIRCULATING WATER PARAMETERS • pH was slightly on higher side on four occasions, we request you please maintain strictly within its specified limit.
• Turbidity was on higher side on 4 occasions and TSS went high up to 70 ppm.
• FRC was well maintained within its specified limit.
• Conductivity was well maintained within the specified limits.
• Total Hardness well maintained within its specified limits.
• CaH was also very well maintained within its specified limits.
• Chloride was well maintained within its specified limits.
• Ortho Phosphate was also very well maintained within the specified limits.
Plant was running smoothly and no any major abnormality was reported except low FRC for three days.
2] COOLING WATER PARAMETERS
Sr. No. | Parameters | Control Limits | Min. | Max. | Avg.
1 | pH | 7.5-8.0 | 7.6 | 8.2 | 7.9
2 | Turbidity | Max. 20 NTU | 13 | 34 | 18.2
3 | FRC | 0.2 - 0.5 ppm | 0.1 | 0.3 | 0.2
4 | TDS | Max. 2100 ppm | 1515 | 1860 | 1697
5 | TH | Max. 1200 ppm | 664 | 857 | 780
6 | Cl | Max. 500 ppm | 167 | 215 | 195
7 | Ortho PO4 | 6.0 - 8.0 ppm | 7 | 8 | 7.6
8 | T. Alk. | Max. 200 ppm | 140 | 195 | 169
9 | Total Iron | Max. 2 ppm | 0.1 | 0.3 | 0.2
10 | Sulphate | Max. 1000 ppm | 775 | 939 | 912.7
11 | SiO2 | 180 ppm | 95 | 120 | 109.9
3] MAKE UP WATER PARAMETERS
Sr. No. | Parameters | Unit | Min. | Max. | Avg.
1 | pH | -- | 7.8 | 8 | 7.9
2 | Turb. | NTU | 2 | 3 | 2.5
3 | Cond | S | 251 | 340 | 304.5
4 | TDS | ppm | 170 | 230 | 206.3
5 | TH | ppm | 106 | 123 | 115.3
6 | Cl | ppm | 36 | 36 | 33
7 | Silica | ppm | 16 | 20 | 18.4
8 | T. Alk. | ppm | 150 | 165 | 158.6
•

## Table 2
3] Monthly Compliance Analysis
Sr. No. | Parameters | Control Limits | < Limits | > Limits | % Complia nce
1 | pH | 7.5-8.0 | 0 | 4 | 87
2 | Turbidity | Max. 20 NTU | -- | 6 | 80
3 | FRC | 0.2 - 0.5 ppm | 1 | 0 | 97
4 | TDS | Max. 2100 ppm | -- | 0 | 100
5 | TH | Max. 1200 ppm | -- | 0 | 100
6 | Cl | Max. 500 ppm | -- | 0 | 100
7 | Ortho PO4 | 6.0 - 8.0 ppm | 0 | 0 | 100
8 | T. Alk. | Max. 200 ppm | -- | 0 | 100
9 | Total Iron | Max. 2 ppm | -- | 0 | 100
10 | Sulphate | Max. 1000 ppm | -- | 0 | 100
11 | SiO2 | 180 ppm | -- | 0 | 100

## Table 3
MAKE UP WATER ANALYSIS
Date | pH | Turb. | Cond | TDS | TH | CaH | Cl | Silica | T. Alk. | P. Alk.
Unit | -- | NTU | us/cm | ppm | ppm | ppm | ppm | ppm | ppm | ppm
2013-07-01 | 7.9 | 3 | 340 | 230 | 120 | 71 | 25 | 19 | 160 | NIL
2013-07-02 | 7.9 | 2 | 325 | 220 | 118 | 70 | 24 | 20 | 160 | NIL
2013-07-03 | 8 | 3 | 310 | 210 | 116 | 68 | 23 | 19 | 162 | NIL
2013-07-04 | 7.9 | 2 | 295 | 200 | 115 | 68 | 21 | 19 | 160 | NIL
2013-07-05 | 7.9 | 2 | 295 | 200 | 115 | 68 | 21 | 19 | 160 | NIL
2013-07-06 | 7.9 | 3 | 325 | 220 | 118 | 69 | 25 | 20 | 155 | NIL
2013-07-07 | 7.8 | 2 | 332 | 225 | 121 | 70 | 28 | 20 | 153 | NIL
2013-07-08 | 7.8 | 3 | 340 | 230 | 123 | 72 | 30 | 20 | 150 | NIL
2013-07-09 | 7.9 | 3 | 340 | 230 | 123 | 72 | 30 | 20 | 155 | NIL
2013-07-10 | 7.9 | 3 | 325 | 220 | 120 | 70 | 28 | 19 | 160 | NIL
2013-07-11 | 8 | 2 | 318 | 215 | 119 | 69 | 27 | 18 | 162 | NIL
2013-07-12 | 7.9 | 3 | 325 | 220 | 120 | 70 | 28 | 19 | 165 | NIL
2013-07-13 | 7.9 | 3 | 332 | 225 | 121 | 70 | 29 | 20 | 162 | NIL
2013-07-14 | 7.9 | 3 | 325 | 220 | 120 | 72 | 30 | 18 | 160 | NIL
2013-07-15 | 7.8 | 2 | 325 | 220 | 120 | 70 | 28 | 19 | 158 | NIL
2013-07-16 | 7.9 | 3 | 317 | 215 | 118 | 69 | 27 | 18 | 160 | NIL
2013-07-17 | 7.9 | 3 | 332 | 225 | 119 | 70 | 29 | 19 | 162 | NIL
2013-07-18 | 7.9 | 2 | 310 | 210 | 117 | 69 | 28 | 18 | 160 | NIL
2013-07-19 | 7.9 | 3 | 325 | 220 | 118 | 69 | 30 | 19 | 162 | NIL
2013-07-20 | 7.9 | 3 | 332 | 225 | 119 | 70 | 29 | 19 | 160 | NIL
2013-07-21 | 7.9 | 2 | 310 | 210 | 115 | 68 | 30 | 19 | 158 | NIL
2013-07-22 | 7.8 | 3 | 295 | 200 | 112 | 67 | 27 | 18 | 160 | NIL
2013-07-23 | 7.8 | 2 | 280 | 190 | 110 | 65 | 25 | 17 | 155 | NIL
2013-07-24 | 7.9 | 2 | 251 | 170 | 106 | 64 | 23 | 16 | 158 | NIL
2013-07-25 | 7.9 | 2 | 273 | 185 | 108 | 65 | 24 | 17 | 160 | NIL
2013-07-26 | 7.9 | 2 | 266 | 180 | 107 | 65 | 23 | 17 | 155 | NIL
2013-07-27 | 7.8 | 2 | 251 | 170 | 106 | 64 | 23 | 16 | 150 | NIL
2013-07-28 | 7.9 | 3 | 258 | 175 | 107 | 65 | 26 | 17 | 155 | NIL
2013-07-29 | 7.9 | 2 | 265 | 180 | 108 | 65 | 24 | 17 | 160 | NIL
2013-07-30 | 7.9 | 2 | 273 | 185 | 109 | 65 | 24 | 17 | 160 | NIL
2013-07-31 | 7.9 | 2 | 251 | 170 | 106 | 64 | 22 | 16 | 160 | NIL
MIN. | 7.8 | 2 | 251 | 170 | 106 | 64 | 36 | 16 | 150 | NIL
MAX. | 8 | 3 | 340 | 230 | 123 | 72 | 36 | 20 | 165 | NIL
AVG. | 7.9 | 2.5 | 305 | 206.3 | 115 | 68 | 33 | 18.4 | 158.6 | #DIV/0!
CWT Monthly Report - JULY-2013

## Table 4
CIRCULATING WATER ANALYSIS FOR COOLING TOWER
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2 | COC
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/c m | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm | Based on TH
2013-07-01 | 7.9 | 34 | 0.2 | 2178 | 1525 | 664 | 344 | 320 | 174 | 7.5 | 175 | NIL | 0.2 | 70 | 775 | 95 | 5.53
2013-07-02 | 8 | 29 | 0.2 | 2164 | 1515 | 742 | 371 | 371 | 167 | 7.4 | 180 | NIL | 0.2 | 59 | 843 | 102 | 6.29
2013-07-03 | 7.9 | 30 | 0.2 | 2300 | 1610 | 750 | 375 | 375 | 178 | 7.5 | 170 | NIL | 0.2 | 62 | 886 | 104 | 6.47
2013-07-04 | 7.9 | 24 | 0.2 | 2335 | 1635 | 733 | 362 | 371 | 171 | 7.5 | 173 | NIL | 0.2 | 50 | 899 | 101 | 6.37
2013-07-05 | 7.8 | 20 | 0.2 | 2412 | 1690 | 721 | 354 | 367 | 167 | 7.6 | 165 | NIL | 0.2 | 43 | 921 | 106 | 6.27
2013-07-06 | 7.9 | 23 | 0.2 | 2571 | 1800 | 824 | 383 | 441 | 196 | 7.6 | 170 | NIL | 0.2 | 40 | 939 | 110 | 6.98
2013-07-07 | 7.9 | 21 | 0.2 | 2447 | 1713 | 857 | 396 | 461 | 214 | 7.5 | 170 | NIL | 0.2 | 35 | 928 | 108 | 7.08
2013-07-08 | 7.9 | 18 | 0.2 | 2600 | 1820 | 815 | 375 | 440 | 207 | 7.4 | 160 | NIL | 0.2 | 32 | 910 | 107 | 6.63
2013-07-09 | 7.9 | 15 | 0.2 | 2527 | 1769 | 803 | 367 | 436 | 205 | 7.3 | 160 | NIL | 0.2 | 30 | 924 | 105 | 6.53
2013-07-10 | 7.9 | 16 | 0.2 | 2500 | 1750 | 836 | 375 | 461 | 203 | 7.4 | 170 | NIL | 0.2 | 33 | 938 | 108 | 6.97
2013-07-11 | 8 | 15 | 0.3 | 2400 | 1680 | 783 | 412 | 371 | 196 | 7.8 | 175 | NIL | 0.3 | 35 | 910 | 113 | 6.58
2013-07-12 | 7.9 | 17 | 0.3 | 2428 | 1700 | 824 | 494 | 330 | 212 | 8 | 170 | NIL | 0.3 | 38 | 927 | 118 | 6.87
2013-07-13 | 7.9 | 16 | 0.2 | 2462 | 1724 | 840 | 507 | 333 | 215 | 7.6 | 168 | NIL | 0.2 | 35 | 939 | 114 | 6.94
2013-07-14 | 7.9 | 16 | 0.2 | 2500 | 1750 | 836 | 375 | 461 | 203 | 7.4 | 175 | NIL | 0.2 | 36 | 938 | 108 | 6.97
2013-07-15 | 8 | 17 | 0.2 | 2564 | 1795 | 803 | 474 | 329 | 201 | 8 | 180 | NIL | 0.2 | 31 | 912 | 109 | 6.69
2013-07-16 | 8.2 | 16 | 0.3 | 2657 | 1860 | 812 | 478 | 334 | 194 | 7.9 | 195 | NIL | 0.2 | 33 | 919 | 112 | 6.88
2013-07-17 | 7.8 | 16 | 0.2 | 2600 | 1820 | 762 | 461 | 301 | 208 | 8 | 150 | NIL | 0.2 | 30 | 898 | 107 | 6.4
2013-07-18 | 7.9 | 16 | 0.2 | 2500 | 1750 | 783 | 445 | 338 | 191 | 7.5 | 165 | NIL | 0.2 | 34 | 904 | 109 | 6.69
2013-07-19 | 7.8 | 16 | 0.2 | 2414 | 1690 | 776 | 424 | 352 | 198 | 7 | 155 | NIL | 0.3 | 36 | 921 | 113 | 6.58
2013-07-20 | 7.9 | 14 | 0.2 | 2357 | 1650 | 750 | 411 | 339 | 194 | 7.6 | 165 | NIL | 0.2 | 30 | 933 | 110 | 6.3
2013-07-21 | 8 | 17 | 0.2 | 2564 | 1795 | 803 | 474 | 329 | 201 | 8 | 175 | NIL | 0.2 | 34 | 912 | 109 | 6.98
2013-07-22 | 7.9 | 17 | 0.3 | 2428 | 1700 | 824 | 494 | 330 | 212 | 8 | 180 | NIL | 0.3 | 38 | 927 | 118 | 7.36
2013-07-23 | 7.7 | 15 | 0.2 | 2328 | 1630 | 721 | 440 | 281 | 191 | 7 | 140 | NIL | 0.2 | 33 | 927 | 107 | 6.55
2013-07-24 | 7.8 | 13 | 0.2 | 2371 | 1660 | 742 | 454 | 288 | 198 | 7.9 | 150 | NIL | 0.2 | 29 | 910 | 111 | 7
2013-07-25 | 7.8 | 16 | 0.2 | 2400 | 1680 | 763 | 577 | 186 | 191 | 7.6 | 160 | NIL | 0.2 | 27 | 916 | 115 | 7.06
2013-07-26 | 7.6 | 18 | 0.1 | 2400 | 1680 | 772 | 580 | 192 | 194 | 7 | 140 | NIL | 0.1 | 25 | 929 | 120 | 7.21
2013-07-27 | 7.9 | 16 | 0.2 | 2331 | 1632 | 755 | 572 | 183 | 188 | 7.5 | 170 | NIL | 0.3 | 23 | 902 | 116 | 7.12
2013-07-28 | 7.9 | 17 | 0.3 | 2511 | 1700 | 824 | 494 | 330 | 212 | 8 | 165 | NIL | 0.3 | 21 | 927 | 118 | 7.7
2013-07-29 | 8.1 | 16 | 0.2 | 2357 | 1650 | 763 | 474 | 289 | 191 | 8 | 185 | NIL | 0.3 | 24 | 928 | 114 | 7.06
2013-07-30 | 8 | 16 | 0.3 | 2271 | 1590 | 750 | 466 | 284 | 181 | 7.9 | 190 | NIL | 0.2 | 26 | 932 | 112 | 6.88
2013-07-31 | 8 | 15 | 0.2 | 2357 | 1650 | 763 | 487 | 276 | 181 | 7.2 | 188 | NIL | 0.2 | 28 | 921 | 109 | 7.2
MIN. | 7.6 | 13 | 0.1 | 2164 | 1515 | 664 | 344 | 183 | 167 | 7 | 140 | 0 | 0.1 | 21 | 775 | 95 | 5.5
MAX. | 8.2 | 34 | 0.3 | 2657 | 1860 | 857 | 580 | 461 | 215 | 8 | 195 | 0 | 0.3 | 70 | 939 | 120 | 7.7
AVG. | 7.9 | 18.2 | 0.2 | 2427 | 1697 | 780 | 442 | 339 | 195 | 7.6 | 169 | #DIV/0! | 0.2 | 35.5 | 913 | 110 | 6.8
CWT Monthly Report - JULY-2013
pH
9.0
8.5
8.0
7.5
7.0
6.5
6.0
Date
Turbidity
200.0
150.0
100.0
50.0
0.0
Date
FRC
1.0
0.8
0.6
0.4
0.2
0.0
Date
Total Hardness
1400
1200
1000
800
600
400
200
Date
CaH
800
700
600
500
400
300
200
100
Date
Chlorides
700
600
500
400
300
200
100
Date
Conductivity
6000
5000
4000
3000
2000
1000
0
Date
TDS
3000
2500
2000
1500
1000
500
0
Date
Iron
2.5
2.0
1.5
1.0
0.5
0.0
Date
Ortho PO4
10.0
8.0
6.0
4.0
2.0
0.0
Date
Suspended Solids
300
225
150
75
0
Date
COC
10.0
8.0
6.0
4.0
2.0
0.0
Date
Total Alk.
500
400
300
200
100
0
Date
Sulphates
1400
1200
1000
800
600
400
200
Date