## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | TSS | FRC | COND | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU |  | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2024-04-01 | 8.3 | 5 |  | NIL | 525 | 352 | 137 | 105 | 32 | 29 | - | - | NIL | - |  |  | 12
2024-04-02 | 8.41 | 9 |  | NIL | 555 | 372 | 146 | 114 | 32 | 36 | - | - | NIL | - |  |  | 15
2024-04-03 | 8.4 | 5 |  | 0.5 | 625 | 419 | 160 | 123 | 37 | 36 | - | - | NIL | - |  |  | 14
2024-04-04 | 8.24 | 9 |  | 0.5 | 607 | 407 | 161 | 112 | 49 | 36 | - | - | NIL | - |  |  | 17
2024-04-05 | 8.14 | 17 |  | 0.6 | 625 | 419 | 165 | 111 | 54 | 37 | - | - | NIL | - |  |  | 18
2024-04-08 | 7.26 | 17 |  | NIL | 729 | 489 | 157 | 103 | 54 | 25 | - | - | NIL | - |  |  | 12
2024-04-09 | 8.11 | 16 |  | NIL | 652 | 437 | 170 | 108 | 62 | 25 | - | - | NIL | - |  |  | 13
2024-04-10 | 8.05 | 16 |  | 0.4 | 739 | 495 | 161 | 103 | 58 | 22 | - | - | NIL | - |  |  | 15
2024-04-11 | 8.6 | 25 |  | 0.4 | 603 | 404 | 157 | 103 | 54 | 29 | - | - | NIL | - |  |  | 12
2024-04-12 | 7.72 | 20 |  | NIL | 764 | 512 | 166 | 108 | 58 | 29 | - | - | NIL | - |  |  | 13
2024-04-18 | 8.15 | 18 |  | NIL | 730 | 489 | 166 | 108 | 58 | 29 | - | - | NIL | - |  |  | 11
2024-04-19 | 8.02 | 14 |  | NIL | 893 | 598 | 175 | 125 | 50 | 36 | - | - | NIL | - |  |  | 11
2024-04-22 | 7.37 | 12 |  | 0.5 | 805 | 540 | 152 | 99 | 53 | 36 | - | - | NIL | - |  |  | 12
2024-04-23 | 7.15 | 6 |  | 0.4 | 801 | 537 | 143 | 90 | 53 | 29 | - | - | NIL | - |  |  | 11
2024-04-24 | 7.46 | 15 |  | 0.5 |  | 585 | 152 | 103 | 49 | 36 | - | - | NIL | - |  |  | 12
2024-04-25 | 7.59 | 14 |  | NIL | 944 | 633 | 157 | 99 | 58 | 29 | - | - | NIL | - |  |  | 11
2024-04-26 | 7.41 | 12 |  | 0.7 | 970 | 650 | 188 | 110 | 78 | 30 | - | - | NIL | - |  |  | 12
2024-04-29 | 7.77 | 17 |  | 0.5 | 989 | 663 | 215 | 112 | 103 | 33 | - | - | NIL | - |  |  | 15
2024-04-30 | 7.45 | 26 |  | 0.5 | 1097 | 735 | 224 | 99 | 125 | 36 | - | - | NIL | - |  |  | 16
2024-05-01 | 7.19 | 26 |  | 0.2 | 1088 | 729 | 220 | 116 | 104 | 36 | - | - | NIL | - |  |  | 15
2024-05-02 | 7.55 | 24 |  | 0.3 | 1193 | 799 | 228 | 130 | 98 | 29 | - | - | NIL | - |  |  | 16
2024-05-03 | 7.22 | 27 |  | 1 | 1152 | 772 | 233 | 112 | 121 | 22 | - | - | NIL | - |  |  | 15
2024-05-04 | 7.7 | 29 |  | 0.6 | 1140 | 764 | 323 | 148 | 175 | 22 | - | - | NIL | - |  |  | 22
2024-05-06 | 7.52 | 26 |  | 0.6 | 1328 | 890 | 831 | 157 | 674 | 33 | - | - | NIL | - |  |  | 19
2024-05-07 | 7.94 | 35 |  | 0.3 | 1418 | 950 | 349 | 143 | 206 | 29 | - | - | NIL | - |  |  | 20
2024-05-08 | 7.1 | 33 |  | 0.2 | 1428 | 957 | 349 | 181 | 168 | 37 | - | - | NIL | - |  |  | 22
2024-05-09 | 7.19 | 53 |  | 0.3 | 1516 | 1016 | 374 | 189 | 185 | 37 | - | - | NIL | - |  |  | 23
2024-05-10 | 7.76 | 21 |  | 1 | 1438 | 964 | 353 | 185 | 168 | 37 | - | - | NIL | - |  |  | 21
2024-05-11 | 7.49 | 32 |  | 0.4 | 1486 | 996 | 374 | 223 | 151 | 44 | - | - | NIL | - |  |  | 36
2024-05-13 | 7.7 | 23 |  | 0.2 | 1515 | 1015 | 391 | 210 | 181 | 37 | - | - | NIL | - |  |  | 34
2024-05-15 | 7.93 | 24 |  | NIL | 1498 | 1004 | 371 | 200 | 171 | 37 | - | - | NIL | - |  |  | 37
2024-05-16 | 7.62 | 20 |  | 0.5 | 1453 | 973 | 379 | 204 | 175 | 37 | - | - | NIL | - |  |  | 35
2024-05-17 | 8.08 | 28 |  | NIL | 1407 | 943 | 375 | 196 | 179 | 37 | - | - | NIL | - |  |  | 24
2024-05-18 | 6.91 | 27 |  | 0.5 |  | 993 | 379 | 184 | 195 | 37 | - | - | NIL | - |  |  | 35
2024-05-20 | 7.86 | 20 |  | NIL | 1492 | 1000 | 396 | 192 | 204 | 37 | - | - | NIL | - |  |  | 32
2024-05-21 | 7.81 | 20 |  | 0.5 | 1462 | 980 | 379 | 200 | 179 | 37 | - | - | NIL | - |  |  | 34
2024-05-22 | 7.38 | 27 |  | NIL | 1501 | 1006 | 388 | 208 | 180 | 37 | - | - | NIL | - |  |  | 33
2024-05-23 | 8.02 | 24 |  | NIL |  | 963 | 392 | 216 | 176 | 29 | - | - | NIL | - |  |  | 39
2024-05-24 | 7.33 | 16 |  | 0.5 | 1495 | 1002 | 384 | 208 | 176 | 29 | - | - | NIL | - |  |  | 31
2024-05-25 | 7.55 | 15 |  | NIL | 1479 | 991 | 445 | 241 | 204 | 33 | - | - | NIL | - |  |  | 39
2024-05-27 | 7.49 | 12 |  | NIL | 1492 | 1000 | 478 | 225 | 253 | 28 | - | - | NIL | - |  |  | 40
2024-05-28 | 7.43 | 16 |  | 0.4 | 1850 | 838 | 483 | 216 | 267 | 26 | - | - | NIL | - |  |  | 41
2024-05-29 | 7.41 | 22 |  | 0.2 | 1441 | 966 | 478 | 241 | 237 | 22 | - | - | NIL | - |  |  | 46
2024-05-30 | 8.03 | 20 |  | 0.1 | 1443 | 967 | 470 | 229 | 241 | 29 | - | - | NIL | - |  |  | 44
2024-05-31 | 8.04 | 16 |  | 0.5 | 1456 | 976 | 483 | 237 | 246 | 29 | - | - | NIL | - |  |  | 45
2024-06-03 | 8.08 | 18 |  | - | 1464 | 990 | 636 | 358 | 278 | 191 | - | - | NIL | - |  |  | -
2024-06-04 | 8.07 | 25 |  | 0.5 | 1505 | 1009 | 674 | 373 | 301 | 206 | - | - | NIL | -
2024-06-05 | 7.51 | 18 |  | 0.5 | 1442 | 966 | 634 | 365 | 269 | 198 | - | - | NIL | -
2024-06-07 | 7.37 | 18 |  | 0.5 | 1418 | 950 | 704 | 394 | 310 | 206 | - | - | NIL | -
2024-06-08 | 7.81 | 17 |  | NIL | 1313 | 880 | 636 | 365 | 271 | 220 | - | - | NIL | -
2024-06-10 |  | 22 |  |  | 1456 | 976 |  |  | 0 |  | - | - | NIL | -
2024-06-11 | 8.21 | 18 |  | NIL | 1216 | 815 | 628 | 343 | 285 | 220 | - | - | NIL | -
2024-06-12 | 8.11 | 18 |  | NIL | 1362 | 913 | 615 | 360 | 255 | 235 | - | - | NIL | -
2024-06-13 | 7.96 | 19 |  | 0.5 | 1544 | 1001 | 628 | 356 | 272 | 228 | - | - | NIL | -
2024-06-14 | 7.64 | 10 |  | 0.5 | 1491 | 999 | 636 | 360 | 276 | 235 | - | - | NIL | -
2024-06-15 | 7.7 | 17 |  | 0.5 | 1471 | 986 | 634 | 374 | 260 | 293 | - | - | NIL | -
2024-06-17 | 7.8 | 12 |  | NIL | 1511 | 1013 | 625 | 401 | 224 | 206 | - | - | NIL | -
2024-06-20 | 7.85 | 25 |  | NIL | 1470 | 985 | 615 | 405 | 210 | 220 | - | - | NIL | -
2024-06-21 | 7.56 | 22 |  | NIL | 1523 | 1021 | 623 | 427 | 196 | 206 | - | - | NIL | -
2024-06-22 | 7.21 | 27 |  | 0.2 | 1435 | 962 | 619 | 392 | 227 | 198 | - | - | NIL | -
2024-06-24 | 7.42 | 26 |  | NIL | 1391 | 932 | 623 | 392 | 231 | 191 | - | - | NIL | -
25.06.24 | 7.04 | 21 |  | NIL | 1631 | 1093 | 650 | 394 | 256 | 184 | - | - | NIL | -
2024-06-26 | 7.27 | 20 |  | NIL | 1398 | 937 | 654 | 385 | 269 | 191 | - | - | NIL | -
2024-06-27 | 7.6 | 47 |  | 0.7 |  | 906 | 659 | 381 | 278 | 384 | - | - | NIL | -
2024-06-28 | 8.14 | 19 |  | NIL | 1270 | 851 | 638 | 370 | 268 | 370 | - | - | NIL | -
2024-06-29 | 6.85 | 17 |  | 0.2 |  | 873 | 550 | 348 | 202 | 156 | - | - | NIL | -
2024-07-01 | 7.56 | 19 |  | NIL | 1292 | 866 | 679 | 370 | 309 | 213 | - | - | NIL | - |  |  | -
2024-07-02 | 7.05 | 25 |  | 0.9 |  | 1597 | 689 | 378 | 311 | 220 | - | - | NIL | -
2024-07-03 | 7.27 | 24 |  | 0.5 | 1344 | 901 | 703 | 396 | 307 | 213 | - | - | NIL | -
2024-07-04 | 7.77 | 33 |  | NIL | 1507 | 1010 | 717 | 415 | 302 | 227 | - | - | NIL | -
2024-07-05 | 7.06 | 33 |  |  | 1288 | 863 | 774 | 396 | 378 | 220 | - | - | NIL | -
2024-07-06 | 7.23 | 18 |  | NIL | 1261 | 845 | 817 | 434 | 383 | 213 | - | - | NIL | -
2024-07-08 | 7.36 | 14 |  | 0.5 | 1271 | 852 | 524 | 295 | 229 | 185 | - | - | NIL | -
2024-07-09 | 7.06 | 14 |  | 0.5 | 1289 | 864 | 547 | 300 | 247 | 178 | - | - | NIL | -
2024-07-10 | 7.69 | 15 |  | NIL | 1326 | 889 | 571 | 309 | 262 | 185 | - | - | NIL | -
2024-07-11 | 6.4 | 20 |  | 0.6 | 1340 | 898 | 590 | 305 | 285 | 78 | - | - | NIL | -
2024-07-12 | 7.51 | 16 |  | NIL | 1291 | 865 | 628 | 343 | 285 | 185 | - | - | NIL | -
2024-07-13 | 7.88 | 17 |  | NIL | 1208 | 810 | 619 | 356 | 263 | 178 | - | - | NIL | -
2024-07-15 | 7.81 | 22 |  | NIL | 1265 | 848 | 565 | 270 | 295 | 203 | - | - | NIL | -
2024-07-16 | 7.77 | 24 |  | 0.2 | 1306 | 875 | 585 | 260 | 325 | 194 | - | - | NIL | -
2024-07-17 | 7.65 | 25 |  | 0.1 | 1283 | 860 | 530 | 245 | 285 | 211 | - | - | NIL | -
2024-07-18 | 7.93 | 21 |  | NIL | 1288 | 863 | 615 | 325 | 290 | 186 | - | - | NIL | -
2024-07-19 | 7.84 | 25 |  |  | 1188 | 796 | 620 | 320 | 300 | 178 | - | - | NIL | -
2024-07-20 | 7.1 | 18 |  | 0.6 | 1258 | 843 | 543 | 262 | 281 | 162 | - | - | NIL | -
2024-07-22 | 7.86 | 20 |  | 0.3 | 1229 | 824 | 585 | 253 | 332 | 186 | - | - | NIL | -
2024-07-23 | 7.74 | 20 |  | NIL | 1285 | 861 | 594 | 257 | 337 | 194 | - | - | NIL | -
2024-07-24 | 6.78 | 22 |  | 0.2 | 1229 | 824 | 580 | 271 | 309 | 178 | - | - | NIL | -
2024-07-25 | 7.14 | 45 |  | NIL | 1250 | 838 | 590 | 281 | 309 | 186 | - | - | NIL | -
2024-07-26 | 7.56 | 31 |  | NIL | 1188 | 796 | 585 | 271 | 314 | 178 | - | - | NIL | -
2024-07-27 | 7.7 | 25 |  | NIL | 1216 | 815 | 580 | 267 | 313 | 186 | - | - | NIL | -
2024-07-29 | 7.35 | 17 |  | NIL | 1253 | 840 | 571 | 220 | 351 | 203 | - | - | NIL | -
2024-07-30 | 6.9 | 21 |  | NIL | 1213 | 813 | 580 | 225 | 355 | 21 | - | - | NIL | -
2024-07-31 | 6.95 | 19 |  | NIL | 1180 | 796 | 571 | 220 | 351 | 203 | - | - | NIL | -
2024-08-01 | 7.22 | 14 |  | NIL | 1165 | 781 | 565 | 203 | 362 | 186 | - | - | NIL | - |  |  | -
2024-08-02 | 7.02 | 11 |  | 0.1 | 1177 | 789 | 551 | 194 | 357 | 194 | - | - | NIL | -
2024-08-03 | 7.09 | 18 |  | 0.6 | 1213 | 813 | 560 | 185 | 375 | 170 | - | - | NIL | -
2024-08-05 | 8.01 | 15 |  | 0.3 | 1328 | 890 | 524 | 194 | 330 | 186 | - | - | NIL | -
2024-08-06 | 7.6 | 11 |  | 0.2 | 1300 | 871 | 520 | 203 | 317 | 203 | - | - | NIL | -
2024-08-07 | 7.8 | 19 |  | 0.5 | 1307 | 876 | 511 | 190 | 321 | 194 | - | - | NIL | -
2024-08-08 | 7.99 | 28 |  | NIL | 1415 | 948 | 533 |  | 533 | 203 | - | - | NIL | -
2024-08-09 | 7.67 | 16 |  | 0.5 | 1271 | 852 | 520 | 194 | 326 | 194 | - | - | NIL | -
2024-08-10 | 7.73 | 31 |  | NIL | 1174 | 787 | 506 | 249 | 257 | 170 | - | - | NIL | -
2024-08-12 | 7.31 | 20 |  | NIL | 1341 | 899 | 461 | 212 | 249 | 170 | - | - | NIL | -
2024-08-13 | 7.83 | 17 |  | NIL | 1380 | 925 | 462 | 356 | 106 | 178 | - | - | NIL | -
2024-08-14 | 7.68 | 19 |  | NIL | 1489 | 998 | 469 | 221 | 248 | 170 | - | - | NIL | -
2024-08-16 | 7.59 | 13 |  | NIL | 1331 | 892 | 279 | 207 | 72 | 170 | - | - | NIL | -
2024-08-17 | 7.28 | 15 |  | 0.3 | 1338 | 897 | 492 | 221 | 271 | 178 | - | - | NIL | -
2024-08-20 | 7.25 | 17 |  | NIL | 1314 | 881 | 474 | 212 | 262 | 170 | - | - | NIL | -
2024-08-21 | 7.44 | 14 |  | NIL | 1334 | 874 | 483 | 285 | 198 | 178 | - | - | NIL | -
22.08.24 | 7.97 | 21 |  | 0.2 | 1257 | 842 | 474 | 207 | 267 | 170 | - | - | NIL | -
2024-08-23 | 7.73 | 33 |  | 0.2 | 1361 | 912 | 481 | 198 | 283 | 162 | - | - | NIL | -
2024-08-24 | 7.78 | 24 |  | 0.5 | 1392 | 933 | 531 | 258 | 273 | 146 | - | - | NIL | -
2024-08-27 | 7.56 | 23 |  | NIL | 1085 | 727 | 460 | 239 | 221 | 122 | - | - | NIL | -
2024-08-28 | 7.23 | 19 |  | NIL | 1052 | 705 | 515 | 253 | 262 | 146 | - | - | NIL | -
29.08.24 | 7.34 | 21 |  | NIL | 986 | 661 | 529 | 217 | 312 | 130 | - | - | NIL | -
2024-08-30 | 6.98 | 22 |  | NIL | 940 | 630 | 520 | 250 | 270 | 138 | - | - | NIL | -
2024-08-31 | 7.59 | 16 |  | NIL | 989 | 663 | 474 | 290 | 184 | 146 | - | - | NIL | -
2024-09-05 | 7.76 | 24 |  | NIL | 1035 | 694 | 462 | 239 | 223 | 138 | - | - | NIL | -
2024-09-06 | 7.21 | 20 |  | NIL | 1029 | 690 | 447 | 224 | 223 | 154 | - | - | NIL | -
07.09.24 | 7.6 | 20 |  | NIL | 1186 | 795 | 457 | 229 | 228 | 162 | - | - | NIL | -
09.09.24 | 7.34 | 34 |  | 0.5 | 1052 | 705 | 462 | 244 | 218 | 138 | - | - | NIL | -
10.09.24 | 7.63 | 45 |  | NIL | 1016 | 681 | 362 | 195 | 167 | 105 | - | - | NIL | -
11.09.24 | 7.46 | 32 |  | NIL | 976 | 654 | 362 | 185 | 177 | 97 | - | - | NIL | -
12.09.24 | 7.36 | 28 |  | NIL | 974 | 653 | 384 | 190 | 194 | 131 | - | - | NIL | -
2024-09-13 | 7.43 | 29 |  | 0.5 | 873 | 585 | 375 | 181 | 194 | 116 | - | - | NIL | -
2024-09-14 | 7.83 | 22 |  | 0.5 | 1334 | 594 | 362 | 190 | 172 | 124 | - | - | NIL | -
2024-09-16 | 7.44 | 23 |  | 0.6 | 876 | 587 | 374 | 178 | 196 | 109 | - | - | NIL | -
2024-09-17 | 7.66 | 25 |  | NIL | 928 | 622 | 394 | 182 | 212 | 138 | - | - | NIL | -
2024-09-18 | 7.6 | 30 |  | 0.5 | 886 | 594 | 389 | 187 | 202 | 109 | - | - | NIL | -
2024-09-19 | 7.73 | 24 |  | NIL | 1023 | 686 | 394 | 192 | 202 | 116 | - | - | NIL | -
2024-09-20 | 7.77 | 26 |  | NIL | 1056 | 708 | 379 | 178 | 201 | 102 | - | - | NIL | -
2024-09-21 | 7.82 | 36 |  | NIL | 1016 | 681 | 371 | 181 | 190 | 122 | - | - | NIL | -
2024-09-23 | 8.02 | 25 |  | NIL | 1120 | 751 | 399 | 162 | 237 | 106 | - | - | NIL | -
24.09.24 | 7.35 | 24 |  | 0.4 | 1067 | 715 | 413 | 153 | 260 | 110 | - | - | NIL | -
2024-09-25 | 8.12 | 45 |  | NIL | 1092 | 732 | 418 | 167 | 251 | 114 | - | - | NIL | -
2024-09-26 | 7.47 | 44 |  | 0.7 | 1071 | 718 | 499 | 165 | 334 | 109 | - | - | NIL | -
2024-09-27 | 7.99 | 58 |  | NIL | 1220 | 818 | 445 | 199 | 246 | 116 | - | - | NIL | -
2024-09-28 | 8.2 | 34 |  | NIL | 1095 | 734 | 379 | 177 | 202 | 109 | - | - | NIL | -
30.09.24 | 7.75 | 19 |  | 0.6 | 1120 | 751 | 402 | 194 | 208 | 116 | - | - | NIL | -
2024-10-01 | 7.18 | 15 |  | NIL | 986 | 661 | 594 | 320 | 274 | 167 | - | - | NIL | - |  |  | -
2024-10-02 | 8.04 | 17 |  | 0.5 | 970 | 650 | 580 | 316 | 264 | 153 | - | - | NIL | -
03.10.24 | 7.82 | 17 |  | NIL | 908 | 609 | 561 | 302 | 259 | 146 | - | - | NIL | -
04.10.24 | 7.96 | 20 |  | NIL | 952 | 638 | 575 | 288 | 287 | 156 | - | - | NIL | -
2024-10-05 | 7.65 | 15 |  | NIL | 976 | 654 | 566 | 302 | 264 | 167 | - | - | NIL | -
2024-10-07 | 7.79 | 18 |  | NIL | 986 | 661 | 557 | 302 | 255 | 138 | - | - | NIL | -
08.10.24 | 7.39 | 34 |  | 0.8 | 1101 | 738 | 579 | 294 | 285 | 160 | - | - | NIL | -
09.10.24 | 7.67 | 19 |  | 0.6 | 982 | 658 | 547 | 285 | 262 | 153 | - | - | NIL | -
10.10.24 | 7.96 | 21 |  | 0.2 | 1032 | 692 | 533 | 280 | 253 | 160 | - | - | NIL | -
11.10.24 | 7.96 | 17 |  | 0.8 | 957 | 641 | 524 | 289 | 235 | 153 | - | - | NIL | -
12.10.24 | 7.81 | 19 |  | 0.2 | 1001 | 671 | 529 | 285 | 244 | 160 | - | - | NIL | -
14.10.24 | 7.89 | 22 |  | 0.1 | 937 | 628 | 333 | 289 | 44 | 167 | - | - | NIL | -
15.10.24 | 7.99 | 22 |  | 1 | 955 | 640 | 538 | 285 | 253 | 153 | - | - | NIL | -
16.10.24 | 8.25 | 17 |  | NIL | 828 | 555 | 441 | 271 | 170 | 146 | - | - | NIL | -
17.10.24 | 7.61 | 15 |  | NIL | 798 | 535 | 452 | 262 | 190 | 138 | - | - | NIL | -
18.10.24 | 8 | 23 |  | 0.9 | 946 | 634 | 473 | 260 | 213 | 153 | - | - | NIL | -
19.10.24 | 8.22 | 26 |  | NIL | 1074 | 720 | 469 | 255 | 214 | 146 | - | - | NIL | -
21.10.24 | 7.99 | 22 |  | NIL | 1025 | 687 | 469 | 255 | 214 | 167 | - | - | NIL | -
22.10.24 | 7.84 | 16 |  | 0.2 | 1018 | 682 | 473 | 246 | 227 | 153 | - | - | NIL | -
23.10.24 | 8.13 | 16 |  | 0.4 | 764 | 512 | 464 | 241 | 223 | 146 | - | - | NIL | -
24.10.24 | 8 | 14 |  | NIL | 1058 | 709 | 475 | 240 | 235 | 160 | - | - | NIL | -
25.10.24 | 8.16 | 16 |  | 0.8 | - | 774 | 484 | 249 | 235 | 167 | - | - | NIL | -
26.10.24 | 8.1 | 15 |  | NIL | 1134 | 760 | 479 | 224 | 255 | 160 | - | - | NIL | -
28.10.24 | 8.07 | 15 |  | NIL | 1201 | 805 | 484 | 249 | 235 | 167 | - | - | NIL | -
29.10.24 | 7.81 | 18 |  | 0.4 | 1211 | 812 | 479 | 240 | 239 | 160 | - | - | NIL | -
30.10.24 | 8 | 18 |  | 0.5 | 1299 | 870 | 461 | 231 | 230 | 153 | - | - | NIL | -
31.10.24 | 7.85 | 16 |  | 0.1 | 1319 | 884 | 441 | 229 | 212 | 167 | - | - | NIL | -
04.11.24 | 7.83 | 17 |  | 0.4 | 1331 | 892 | 445 | 225 | 220 | 153 | - | - | NIL | - |  |  | -
05.11.24 | 7.81 | 17 |  | 0.2 | 1289 | 864 | 453 | 222 | 231 | 167 | - | - | NIL | - |  |  | -
06.11.24 | 7.52 | 16 |  | 0.6 | 1311 | 879 | 445 | 218 | 227 | 160 | - | - | NIL | - |  |  | -
07.11.24 | 7.69 | 19 |  | NIL | 1316 | 882 | 453 | 221 | 232 | 167 | - | - | NIL | - |  |  | -
08.11.24 | 7.83 | 19 |  | NIL | 1210 | 811 | 449 | 233 | 216 | 160 | - | - | NIL | - |  |  | -
09.11.24 | 7.64 | 12 |  | 0.6 | 1244 | 834 | 453 | 229 | 224 | 153 | - | - | NIL | - |  |  | -
11.11.24 | 7.57 | 15 |  | 0.4 | 1177 | 789 | 462 | 220 | 242 | 167 | - | - | NIL | - |  |  | -
12.11.24 | 8.07 | 15 |  | NIL | 1225 | 821 | 458 | 224 | 234 | 182 | - | - | NIL | - |  |  | -
13.11.24 | 7.84 | 20 |  | 0.2 | 1310 | 878 | 441 | 216 | 225 | 175 | - | - | NIL | - |  |  | -
14.11.24 | 8.17 | 19 |  | 0.2 | 1311 | 879 | 453 | 208 | 245 | 166 | - | - | NIL | - |  |  | -
15.11.24 | 8.52 | 17 |  | 0.1 | 1234 | 827 | 441 | 220 | 221 | 146 | - | - | NIL | - |  |  | -
16.11.24 | 7.65 | 17 |  | 0.1 | 1249 | 837 | 433 | 208 | 225 | 153 | - | - | NIL | - |  |  | -
18.11.24 | 7.87 | 18 |  | 0.2 | 1271 | 852 | 437 | 216 | 221 | 153 | - | - | NIL | - |  |  | -
19.11.24 | 7.56 | 16 |  | NIL | 1243 | 833 | 441 | 220 | 221 | 160 | - | - | NIL | - |  |  | -
20.11.24 | 7.75 | 14 |  | 0.5 | 1188 | 796 | 437 | 225 | 212 | 153 | - | - | NIL | - |  |  | -
21.11.24 | 7.24 | 16 |  | NIL | 1232 | 826 | 433 | 216 | 217 | 160 | - | - | NIL | - |  |  | -
22.11.24 | 6.92 | 18 |  | 0.6 | 1207 | 809 | 424 | 220 | 204 | 153 | - | - | NIL | - |  |  | -
23.11.24 | 7.63 | 18 |  | 0.4 |  | 853 | 441 | 223 | 218 | 160 | - | - | NIL | - |  |  | -
25.11.24 | 8.84 | 15 |  | NIL | 1214 | 814 | 441 | 223 | 218 | 160 | - | - | NIL | - |  |  | -
26.11.24 | 7.53 | 18 |  | 0.8 | 1215 | 814 | 445 | 227 | 218 | 160 | - | - | NIL | - |  |  | -
27.11.24 | 7.08 | 16 |  | 0.7 | 1225 | 821 | 454 | 235 | 219 | 167 | - | - | NIL | - |  |  | -
28.11.24 | 7.7 | 15 |  | NIL | 1305 | 875 | 462 | 244 | 218 | 175 | - | - | NIL | - |  |  | -
29.11.24 | 8.41 | 18 |  | 0.2 | 1290 | 864 | 454 | 239 | 215 | 175 | - | - | NIL | - |  |  | -
30.11.24 | 7.11 | 15 |  | NIL | 1298 | 870 | 458 | 248 | 210 | 160 | - | - | NIL | - |  |  | -
02.12.24 | 7.79 | 25 |  | 1 | 1400 | 938 | 471 | 237 | 234 | 167 | - | - | NIL | - |  |  | -
03.12.24 | 8.04 | 15 |  | 0.5 | 1348 | 903 | 466 | 220 | 246 | 153 | - | - | NIL | - |  |  | -
04.12.24 | 7.83 | 26 |  | Nil | 1405 | 942 | 471 | 229 | 242 | 160 | - | - | NIL | - |  |  | -
05.12.24 | 7.8 | 21 |  | 0.4 |  | 1007 | 483 | 237 | 246 | 146 | - | - | NIL | - |  |  | -
06.12.24 | 8.02 | 21 |  | Nil | 1503 | 1007 | 483 | 237 | 246 | 167 | - | - | NIL | - |  |  | -
07.12.24 | 8.59 | 5 |  | Nil | 1400 | 938 | 601 | 315 | 286 | 160 | - | - | NIL | - |  |  | -
09.12.24 | 7.99 | 30 |  | Nil | 1300 | 871 | 466 | 298 | 168 | 160 | - | - | NIL | - |  |  | -
10.12.24 | 7.77 | 32 |  | 0.6 | 1333 | 893 | 454 | 294 | 160 | 153 | - | - | NIL | - |  |  | -
11.12.24 | 7.85 | 34 |  | 0.5 | 1247 | 836 | 458 | 302 | 156 | 160 | - | - | NIL | - |  |  | -
12.12.24 | 7.74 | 28 |  | 0.7 | 1190 | 797 | 454 | 298 | 156 | 153 | - | - | NIL | - |  |  | -
13.12.24 | 8.08 | 27 |  | Nil | 1262 | 846 | 462 | 356 | 106 | 153 | - | - | NIL | - |  |  | -
14.12.24 | 7.65 | 39 |  | Nil | 1268 | 850 | 449 | 293 | 156 | 160 | - | - | NIL | - |  |  | -
16.12.24 | 8.14 | 27 |  | Nil | 1167 | 782 | 424 | 288 | 136 | 156 | - | - | NIL | - |  |  | -
17.12.24 | 8.4 | 30 |  | Nil | 1261 | 845 | 420 | 297 | 123 | 146 | - | - | NIL | - |  |  | -
18.12.24 | 8.03 | 19 |  | 0.6 | 1191 | 798 | 412 | 247 | 165 | 138 | - | - | NIL | - |  |  | -
19.12.24 | 8.43 | 23 |  | Nil | 1217 | 816 | 420 | 298 | 122 | 131 | - | - | NIL | - |  |  | -
20.12.24 | 7.96 | 18 |  | 0.2 | 1267 | 849 | 416 | 283 | 133 | 146 | - | - | NIL | - |  |  | -
21.12.24 | 7.25 | 22 |  | 0.5 |  | 821 | 412 | 270 | 142 | 160 | - | - | NIL | - |  |  | -
23.12.24 | 8.68 | 27 |  | Nil | 1326 | 889 | 432 | 261 | 171 | 153 | - | - | NIL | - |  |  | -
24.12.24 | 7.98 | 22 |  | 0.8 | 1300 | 871 | 424 | 253 | 171 | 146 | - | - | NIL | - |  |  | -
25.12.24 | 7.83 | 24 |  | 0.1 | 1359 | 911 | 428 | 265 | 163 | 160 | - | - | NIL | - |  |  | -
26.12.24 | 7.72 | 24 |  | 0.6 | 1404 | 941 | 432 | 257 | 175 | 153 | - | - | NIL | - |  |  | -
27.12.24 | 7.31 | 38 |  | 1 | 1471 | 986 | 445 | 273 | 172 | 167 | - | - | NIL | - |  |  | -
28.12.24 | 7.98 | 35 |  | Nil | 1297 | 869 | 416 | 253 | 163 | 153 | - | - | NIL | - |  |  | -
30.12.24 | 7.48 | 26 |  | Nil | 1452 | 973 | 469 | 287 | 182 | 146 | - | - | NIL | - |  |  | -
31.12.24 | 7.31 | 16 |  | Nil | 1429 | 958 | 445 | 278 | 167 | 153 | - | - | NIL | - |  |  | -
01.01.25 | 8.1 | 18 |  | NIL | 1411 | 946 | 488 | 298 | 190 | 155 | - | - | NIL | - |  |  | -
02.01.25 | 7.9 | - |  | NIL | 1425 | 955 | 493 | 320 | 173 | 182 | - | - | NIL | - |  |  | -
03.01.25 | 7.9 | 28 |  | NIL | 1453 | 974 | 511 | 329 | 182 | 196 | - | - | NIL | - |  |  | -
04.01.25 | 8.08 | 42 |  | 0.2 | 1408 | 944 | 502 | 302 | 200 | 187 | - | - | NIL | - |  |  | -
06.01.25 | 7.88 | 27 |  | NIL |  | 900 | 506 | 324 | 182 | 179 | - | - | NIL | - |  |  | -
07.01.25 | 7.97 | 29 |  | NIL | 1349 | 904 | 497 | 311 | 186 | 158 | - | - | NIL | - |  |  | -
08.01.25 | 7.96 | 17 |  | NIL | 1353 | 907 | 511 | 320 | 191 | 144 | - | - | NIL | - |  |  | -
09.01.25 | 7.98 | 23 |  | NIL | 1455 | 975 | 515 | 315 | 200 | 165 | - | - | NIL | - |  |  | -
10.01.25 | 7.87 | 21 |  | 0.8 | 1501 | 1006 | 506 | 324 | 182 | 151 | - | - | NIL | - |  |  | -
11.01.25 | 8.17 | 29 |  | NIL | 1539 | 1031 | 511 | 320 | 191 | 144 | - | - | NIL | - |  |  | -
13.01.25 | 8.03 | 24 |  | 0.2 | 1495 | 1002 | 502 | 315 | 187 | 158 | - | - | NIL | - |  |  | -
15.01.25 | 8.05 | 22 |  | 0.5 | 1501 | 1006 | 502 | 315 | 187 | 158 | - | - | NIL | - |  |  | -
16.01.25 | 8.28 | 24 |  | NIL | 1440 | 965 | 534 | 325 | 209 | 172 | - | - | NIL | - |  |  | -
17.01.25 | 7.94 | 14 |  | 0.6 | 1404 | 941 | 524 | 278 | 246 | 165 | - | - | NIL | - |  |  | -
18.01.25 | 8.35 | 16 |  | NIL | 1445 | 968 | 538 | 278 | 260 | 158 | - | - | NIL | - |  |  | -
20.01.25 | 8.23 | 20 |  | 1 | 1528 | 1024 | 534 | 283 | 251 | 158 | - | - | NIL | - |  |  | -
21.01.25 | 7.85 | 20 |  | NIL | 1532 | 1027 | 538 | 302 | 236 | 165 | - | - | NIL | - |  |  | -
22.01.25 | 7.88 | 25 |  | 0.8 | 1516 | 1016 | 548 | 288 | 260 | 187 | - | - | NIL | - |  |  | -
23.01.25 | 7.95 | 23 |  | 0.5 | 1529 | 1025 | 552 | 278 | 274 | 172 | - | - | NIL | - |  |  | -
24.01.25 | 8.2 | 29 |  | NIL | 1435 | 962 | 543 | 292 | 251 | 172 | - | - | NIL | - |  |  | -
25.01.25 | 8.14 | 31 |  | NIL | 1467 | 983 | 571 | 298 | 273 | 187 | - | - | NIL | - |  |  | -
27.01.25 | 7.86 | 17 |  | NIL | 1494 | 1001 | 552 | 300 | 252 | 165 | - | - | NIL | - |  |  | -
28.01.25 | 7.77 | 21 |  | NIL | 1553 | 1041 | 547 | 293 | 254 | 158 | - | - | NIL | - |  |  | -
29.01.25 | 8.15 | 24 |  | 0.5 | 1626 | 1090 | 571 | 302 | 269 | 172 | - | - | NIL | - |  |  | -
30.01.25 | 8.7 | 18 |  | NIL | 1702 | 1141 | 576 | 312 | 264 | 187 | - | - | NIL | - |  |  | -
31.01.25 | 8.13 | 16 |  | NIL | 1561 | 1046 | 566 | 307 | 259 | 165 | - | - | NIL | - |  |  | -
01.02.25 | 8.05 | 19 |  | 1 | 1594 | 1068 | 534 | 304 | 230 | 194 | - | - | NIL | - |  |  | -
03.02.25 | 8.28 | 22 |  | 0.5 | 1567 | 1050 | 713 | 396 | 317 | 178 | 6.7 | - | NIL | - |  |  | -
04.02.25 | 7.94 | 26 |  | 0.5 | 1600 | 1072 | 722 | 400 | 322 | 194 | 6.7 | - | NIL | - |  |  | -
05.02.25 | 7.88 | 27 |  | 0.9 | 1593 | 1067 | 713 | 396 | 317 | 178 | 6.2 | - | NIL | - |  |  | -
06.02.25 | 8.07 | 21 |  | 0.5 | 1790 | 1199 | 727 | 391 | 336 | 203 | 6 | - | NIL | - |  |  | -
07.02.25 | 7.35 | 21 |  | 1 | 1737 | 1164 | 702 | 369 | 333 | 179 | 6.2 | - | NIL | - |  |  | -
08.02.25 | 8.29 | 22 |  | NIL | 1685 | 1129 | 706 | 377 | 329 | 165 | 6.4 | - | NIL | - |  |  | -
10.02.25 | 7.77 | 18 |  | NIL | 1620 | 1086 | 733 | 383 | 350 | 172 | 6.1 | - | NIL | - |  |  | -
11.02.25 | 7.86 | 20 |  | 0.1 | 1711 | 1147 | 857 | 377 | 480 | 158 | - | - | NIL | - |  |  | -
12.02.25 | 7.76 | 21 |  | 0.4 | 1690 | 1132 | 848 | 382 | 466 | 165 | 6.4 | - | NIL | - |  |  | -
13.02.25 | 8 | 18 |  | 0.5 | 1840 | 1233 | 846 | 422 | 424 | 179 | - | - | NIL | - |  |  | -
14.02.25 | 8.12 | 11 |  | NIL | 1648 | 1104 | 839 | 391 | 448 | 179 | 6 | - | NIL | - |  |  | -
15.02.25 | 7.8 | 12 |  | NIL | 1695 | 1136 | 826 | 382 | 444 | 165 | 6.2 | - | NIL | - |  |  | -
17.02.25 | 7.8 | 13 |  | 1 | 1755 | 1176 | 821 | 361 | 460 | 172 | 6.2 | - | NIL | - |  |  | -
18.02.25 | 8.12 | 20 |  | 0.2 | 1780 | 1193 | 826 | 364 | 462 | 158 | - | - | NIL | - |  |  | -
19.02.25 | 8.16 | 20 |  | 0.2 | 1628 | 1091 | 809 | 438 | 371 | 143 | - | - | NIL | - |  |  | -
20.02.25 | 8.02 | 20 |  | NIL | 1676 | 1123 | 833 | 452 | 381 | 179 | - | - | NIL | - |  |  | -
21.02.25 | 8.22 | 25 |  | NIL | 1653 | 1108 | 823 | 443 | 380 | 165 | - | - | NIL | - |  |  | -
22.02.25 | 8.17 | 20 |  | 0.6 | 1556 | 1043 | 833 | 442 | 391 | 172 | - | - | NIL | - |  |  | -
24.02.25 | 8.36 | 18 |  | NIL | 1568 | 1051 | 830 | 435 | 395 | 161 | - | - | NIL | - |  |  | -
25.02.25 | 8.38 | 20 |  | 0.5 | 1625 | 1089 | 805 | 451 | 354 | 194 | - | - | NIL | - |  |  | -
27.02.25 | 8.46 | 22 |  | NIL | 1594 | 1068 | 804 | 454 | 350 | 151 | - | - | NIL | - |  |  | -
28.02.25 | 8.15 | 17 |  | 0.2 | 1635 | 1096 | 799 | 445 | 354 | 158 | - | - | NIL | - |  |  | -
01.03.25 | 8.33 | 18 |  | 0.5 | 1614 | 1082 | 795 | 449 | 346 | 172 | - | - | NIL | - |  |  | -
03.03.25 | 8.31 | 30 |  | 0.5 | 1576 | 1056 | 648 | 389 | 259 | 178 | - | - | NIL | - |  |  | -
04.03.25 | 8.04 | 23 |  | 0.1 | 1514 | 1015 | 702 | 402 | 300 | 187 | - | - | NIL | - |  |  | -
05.03.25 | 8.14 | 26 |  | NIL | 1405 | 942 | 734 | 410 | 324 | 195 | - | - | NIL | - |  |  | -
06.03.25 | 8.13 | 22 |  | NIL | 1416 | 949 | 756 | 428 | 328 | 178 | - | - | NIL | - |  |  | -
07.03.25 | SHUT DOWN
08.03.25 | SHUT DOWN
10.03.25 | 7.61 | 26 |  | 0.6 | 1426 | 956 | 729 | 399 | 330 | 195 | 3.1 | - | NIL | - |  |  | 28
11.03.25 | 7.96 | 16 |  | 0.1 | 1515 | 1015 | 739 | 418 | 321 | 178 | 3.4 | - | NIL | - |  |  | 24
12.03.25 | 7.91 | 23 |  | NIL | 1444 | 968 | 748 | 422 | 326 | 204 | 3.2 | - | NIL | - |  |  | 27
13.03.25 | 7.45 | 28 |  | NIL | 1549 | 1038 | 712 | 405 | 307 | 213 | 3.1 | - | NIL | - |  |  | 22
15.03.25 | 8.22 | 20 |  | NIL | 1450 | 972 | 728 | 392 | 336 | 195 | 3.2 | - | NIL | - |  |  | 25
17.03.25 | 8.39 | 23 |  | NIL | 1574 | 1055 | 651 | 374 | 277 | 204 | 3 | - | NIL | - |  |  | 27
18.03.25 | 8.05 | 21 |  | 0.1 | 1541 | 1033 | 673 | 387 | 286 | 187 | 3.3 | - | NIL | - |  |  | 29
19.03.25 | 8.23 | 29 |  | 0.3 | 1626 | 1090 | 704 | 396 | 308 | 204 | 3.6 |  | NIL |  |  |  | 32
20.03.25 | 8.16 | 27 |  | NIL | 1710 | 1146 | 717 | 405 | 312 | 213 | 3.8 | - | NIL |  |  |  | 30
21.03.25 | 7.88 | 20 |  | NIL | 1759 | 1179 | 708 | 392 | 316 | 195 | 3.2 | - | NIL |  |  |  | 28
22.03.25 | 8.23 | 33 |  | NIL | 1665 | 1116 | 704 | 387 | 317 | 187 | 3 | - | NIL |  |  |  | 25
24.03.25 | 7.95 | 22 |  | NIL | 1759 | 1179 | 708 | 374 | 334 | 187 | 3.1 | - | NIL |  |  |  | 26
25.03.25 | 7.81 | 22 |  | NIL | 1781 | 1193 | 874 | 506 | 368 | 204 | 3.3 | - | NIL |  |  |  | 23
26.03.25 | 7.79 | 18 |  | NIL | 1876 | 1258 | 897 | 515 | 382 | 192 | 3.2 | - | NIL |  |  |  | 19
27.03.25 | 8.04 | 21 |  | NIL | 1826 | 1224 | 920 | 524 | 396 | 199 | 3.4 | - | NIL |  |  |  | 21
28.03.25 | 8.1 | 19 |  | NIL | 1776 | 1190 | 911 | 511 | 400 | 185 | 3.2 | - | NIL |  |  |  | 18
29.03.25 | 8.39 | 22 |  | 0.5 | 1832 | 1228 | 925 | 520 | 405 | 178 | 3.4 | - | NIL |  |  |  | 20
31.03.25 | 8.2 | 23 |  | 0.3 | 1916 | 1284 | 879 | 460 | 419 | 151 | 3.1 | - | NIL |  |  |  | 21
01.04.25 | 8.21 | 15 |  | 0.2 | 1992 | 1335 | 630 | 331 | 299 | 197 | 4.2 | - | NIL | - |  |  | -
02.04.25 | 8.21 | 19 |  | 0.3 | 1867 | 1252 | 607 | 322 | 285 | 181 | 4.3 | - | - |  |  |  | 28
03.04.25 | 7.29 | 16 |  | NIL | 1956 | 1311 | 639 | 363 | 276 | 187 | 4.1 | - | - | - |  |  | 24
04.04.25 | 8.53 | 26 |  | NIL | 1988 | 1332 | 653 | 368 | 285 | 181 | 4.1 | - | - | - |  |  | 22
05.04.25 | 8.38 | 18 |  | NIL | 2027 | 1358 | 644 | 377 | 267 | 197 | 4.4 | - | - | - |  |  | 24
07.04.25 | 8.46 | 20 |  | NIL | 2070 | 1387 | 704 | 382 | 322 | 197 | 4.3 | - | - | - |  |  | 26
08.04.25 | 8.41 | 25 |  | 0.1 | 2140 | 1434 | 736 | 432 | 304 | 205 | 4.2 | - | - | - |  |  | 22
09.04.25 | 8.65 | 21 |  | 0.4 | 2124 | 1422 | 782 | 423 | 359 | 197 | 4.5 | - | - | - |  |  | 20
10.04.25 | 8.08 | 21 |  | NIL | 1896 | 1270 | 787 | 428 | 359 | 205 | 4.3 | - | - | - |  |  | 21
11.04.25 | 7.26 | 18 |  | NIL | 2046 | 1371 | 796 | 419 | 377 | 173 | 4.5 | - | - | - |  |  | 19
12.04.25 | 8.12 | 20 |  | 0.2 | 2141 | 1435 | 805 | 428 | 377 | 189 | 4.4 | - | - | - |  |  | 18
14.04.25 | 8.15 | 19 |  | 0.1 | 1611 | 1080 | 791 | 428 | 363 | 173 | 4.5 | - | - | - |  |  | 22
15.04.25 | 8.56 | 19 |  | 0.1 | 1765 | 1183 | 805 | 428 | 377 | 189 | 4.6 | - | - | - |  |  | 25
16.04.25 | 8.1 | 22 |  | NIL | 1901 | 1274 | 800 | 414 | 386 | 205 | 4.3 | - | - | - |  |  | 23
17.04.25 | 7.68 | 25 |  | 0.4 | 1835 | 1230 | 819 | 428 | 391 | 205 | 4.6 | - | - | - |  |  | 21
18.04.25 | 7.98 | 24 |  | 0.1 | 1870 | 1253 | 810 | 432 | 378 | 197 | 4.3 | - | - | - |  |  | 22
19.04.25 | 6.96 | 24 |  | NIL | 2007 | 1345 | 828 | 428 | 400 | 181 | 4.5 | - | - | - |  |  | 19
21.04.25 | 8.14 | 19 |  | 0.1 | 1820 | 1220 | 809 | 424 | 385 | 157 | 4.7 | - | - | - |  |  | 18
22.04.25 | 8.18 | 18 |  | 0.3 | 1497 | 1003 | 862 | 405 | 457 | 165 | 4.5 | - | - | - |  |  | 20
23.04.25 | 8.02 | 21 |  | 0.3 | 1431 | 959 | 785 | 414 | 371 | 181 | 4.6 | - | - | - |  |  | 21
24.04.25 | 7.34 | 21 |  | 0.2 | 1391 | 932 | 800 | 409 | 391 | 197 | 4.4 | - | - | - |  |  | 20
25.04.25 | 7.87 | 20 |  | NIL | 1746 | 1170 | 785 | 390 | 395 | 176 | 4.6 | - | - | - |  |  | 17
26.04.25 | 8.19 | 18 |  | NIL | 1528 | 1024 | 781 | 386 | 395 | 165 | 4.4 | - | - | - |  |  | 19
28.04.25 | 7.95 | 21 |  | 0.3 |  | 935 | 790 | 388 | 402 | 161 | 4.6 | - | - | - |  |  | 17
29.04.25 | 7.89 | 21 |  | 0.2 | 1450 | 972 | 818 | 347 | 471 | 188 | 4.8 | - | - | - |  |  | 18
30.04.25 | 7.84 | 22 |  | 0.6 | 1395 | 935 | 734 | 360 | 374 | 157 | 4.5 | - | - | - |  |  | 16
01.05.25 | 8.1 | 19 |  | 0.1 | 1356 | 909 | 714 | 306 | 408 | 142 | 4 | - | - | - |  |  | 24
02.05.25 | 8.06 | 18 |  | 0.1 | 1361 | 912 | 694 | 394 | 300 | 157 | 4.2 | - | - | - |  |  | 18
03.05.25 | 8.01 | 21 |  | 0.5 | 1325 | 888 | 698 | 398 | 300 | 165 | 4 | - | - | - |  |  | 20
05.05.25 | 7.83 | 20 |  | 0.2 | 1371 | 919 | 694 | 388 | 306 | 165 | 4.5 | - | - | - |  |  | 15
06.05.25 | 7.71 | 23 |  | 0.5 | 1323 | 887 | 673 | 371 | 302 | 154 | 4.3 | - | - | - |  |  | 16
07.05.25 | 7.7 | 20 |  | 0.4 | 1174 | 787 | 694 | 384 | 310 | 181 | 4.6 | - | - | - |  |  | 18
08.05.25 | 7.58 | 19 |  | 0.2 | 1451 | 972 | 602 | 521 | 81 | 197 | 4.5 | - | - | - |  |  | 16
09.05.25 | 7.71 | 18 |  | 0.5 | 1252 | 839 | 595 | 317 | 278 | 181 | 4.2 | - | - | - |  |  | 15
10.05.25 | 7.92 | 22 |  | Nil | 1309 | 877 | 598 | 321 | 277 | 189 | 4.1 | - | - | - |  |  | 14
12.05.25 | 7.95 | 20 |  | 0.2 | 1208 | 810 | 598 | 329 | 269 | 160 | 4.4 | - | - | - |  |  | 15
13.05.25 | 7.8 | 20 |  | 0.2 | 1179 | 790 | 574 | 356 | 218 | 173 | 4 | - | - | - |  |  | 17
14.05.25 | 7.77 | 25 |  | 0.4 | 1114 | 747 | 594 | 329 | 265 | 197 | 4.3 | - | - | - |  |  | 18
15.05.25 | 8.16 | 18 |  | 0.5 | 1095 | 734 | 586 | 325 | 261 | 181 | 4.1 | - | - | - |  |  | 26
16.05.25 | 8.05 | 22 |  | 0.1 | 1095 | 734 | 578 | 321 | 257 | 173 | 4.2 | - | - | - |  |  | 16
17.05.25 | 7.73 | 21 |  | Nil | 1414 | 948 | 572 | 317 | 255 | 169 | 4.3 | - | - | - |  |  | 18
19.05.25 | 7.66 | 19 |  | Nil | 1182 | 792 | 572 | 317 | 255 | 165 | 4.3 | - | - | - |  |  | 16
20.05.25 | 7.93 | 21 |  | 0.4 | 1188 | 796 | 554 | 326 | 228 | 181 | 4.1 | - | - | - |  |  | 15
21.05.25 | 7.51 | 21 |  | 0.4 | 1389 | 931 | 541 | 330 | 211 | 173 | 4.2 | - | - | - |  |  | 15
22.05.25 | 7.81 | 21 |  | 0.5 | 1294 | 867 | 515 | 312 | 203 | 165 | 4 | - | - | - |  |  | 17
23.05.25 | 7.64 | 19 |  | 0.6 | 1474 | 988 | 524 | 317 | 207 | 170 | 4.5 | - | - | - |  |  | 19
24.05.25 | 7.84 | 20 |  | 0.5 | 1540 | 1032 | 546 | 326 | 220 | 162 | 4.4 | - | - | - |  |  | 18
27.05.25 | 7.4 | 22 |  | 0.2 | 1555 | 1042 | 532 | 307 | 225 | 155 | 4.1 | - | - | - |  |  | 17
28.05.25 | 7.36 | 21 |  | 0.3 | 1231 | 825 | 546 | 321 | 225 | 170 | 4.2 | - | - | - |  |  | 16
29.05.25 | 7.22 | 18 |  | 0.1 | 1422 | 953 | 581 | 308 | 273 | 151 | 4.5 | - | - | - |  |  | 19
30.05.25 | 7.52 | 20 |  | Nil | 1386 | 929 | 585 | 312 | 273 | 158 | 4.6 | - | - | - |  |  | 20
31.05.25 | 7.26 | 23 |  | 0.2 | 1485 | 995 | 616 | 321 | 295 | 165 | 4.5 | - | - | - |  |  | 21
02.06.25 | 7.37 | 18 |  | 0.3 | 1322 | 886 | 625 | 323 | 302 | 158 | 4.2 | - | - | - |  |  | 24
03.06.25 | 7.02 | 21 |  | 0.3 | 1507 | 1010 | 633 | 330 | 303 | 165 | 4.1 | - | - | - |  |  | 26
04.06.25 | 7.05 | 21 |  | 0.7 | 1455 | 975 | 642 | 334 | 308 | 180 | 4.2 | - | - | - |  |  | 25
05.06.25 | 7.55 | 23 |  | NIL | 1332 | 893 | 636 | 340 | 296 | 187 | 4.6 | - | - | - |  |  | 22
06.06.25 | 6.76 | 20 |  | 0.9 | 1329 | 891 | 641 | 336 | 305 | 180 | 4.3 | - | - | - |  |  | 26
07.06.25 | 7.25 | 49 |  | 0.5 | 1277 | 856 | 654 | 323 | 331 | 151 | 4.6 | - | - | - |  |  | 22
09.06.25 | 7.4 | 26 |  | 0.3 | 1365 | 915 | 609 | 323 | 286 | 153 | 4.6 | - | - | - |  |  | 23
10.06.25 | 7.08 | 35 |  | 0.4 | 1389 | 931 | 597 | 309 | 288 | 157 | 4.5 | - | - | - |  |  | 25
11.06.25 | 7.75 | 38 |  | 0.5 | 1485 | 995 | 602 | 313 | 289 | 167 | 4.6 | - | - | - |  |  | 27
12.06.25 | 7.6 | 64 | 38 | 0.7 | 960 | 643 | 410 | 266 | 144 | 280 | 4.9 | 45 | - | - |  |  | -
13.06.25 | 7.6 | 52 | 34 | 0.6 | 930 | 623 | 400 | 254 | 146 | 283 | 4.8 | 48 | - | - |  |  | -
14.06.25 | 7.6 | - | 51 | 0.6 | 900 | 603 | 395 | 244 | 151 | 272 | 4.4 | 50 | - | 0.3 |  |  | -
16.06.25 | 8.1 | - | 35 | NIL | 831 | 556 | 358 | 212 | 146 | 203 | 6 | 53 | - | 0.3 |  |  | -
17.06.25 | 8.3 | - | 25 | NIL | 775 | 519 | 265 | 167 | 98 | 210 | 6.3 | 67 | - | 0.3 |  |  | -
18.06.25 | 8.77 | - | 23 | NIL | 937 | 628 | 643 | 405 | 238 | 157 | 4.3 | - | - | - |  |  | 26
19.06.25 | 8.22 | - | 23 | NIL | 900 | 603 | 628 | 395 | 233 | 150 | 4.6 | - | - | - |  |  | 25
20.06.25 | 7.56 | - | 18 | 0.2 | 913 | 612 | 638 | 395 | 243 | 157 | 4.5 | - | - | - |  |  | 25
21.06.25 | 7.45 | - | 20 | 0.3 | 983 | 659 | 633 | 390 | 243 | 150 | 4.4 | - | - | - |  |  | 28
23.06.25 | 6.22 | - | 20 | 0.2 | 970 | 650 | 647 | 391 | 256 | 142 | 4.5 | - | - | - |  |  | 26
24.06.25 | 7.25 | - | 23 | NIL | 1080 | 724 | 652 | 395 | 257 | 157 | 4.5 | - | - | 0.1 |  |  | 29
25.06.25 | 7.18 | - | 22 | 0.2 | 1073 | 719 | 655 | 361 | 294 | 150 | 4.7 | - | - | - |  |  | 25
26.06.25 | 7.82 | - | 18 | NIL | 1005 | 679 | 664 | 357 | 307 | 157 | 4.6 | - | - | - |  |  | 24
27.06.25 | 7.3 | - | 22 | NIL | 1047 | 702 | 672 | 357 | 315 | 164 | 4.3 | - | - | - |  |  | 26
28.06.25 | 7.59 | - | 19 | 0.4 | 1035 | 694 | 664 | 349 | 315 | 157 | 4.4 | - | - | - |  |  | 22
30.06.25 | 7.93 | - | 22 | 0.1 | 868 | 582 | 678 | 352 | 326 | 164 | 4.3 | - | - | - |  |  | 24
01.07.25 | 7.25 | - | 22 | 0.1 | 1088 | 729 | 674 | 352 | 322 | 157 | 4.2 | - | - | - |  |  | 25
02.07.25 | 7.89 | - | 21 | Nil | 1059 | 710 | 700 | 360 | 340 | 178 | 4.3 | - | - | - |  |  | 21
03.07.25 | 7.67 | - | 16 | 0.5 | 1059 | 710 | 640 | 354 | 286 | 177 | 4.5 | - | - | - |  |  | 20
04.07.25 | 7.74 | - | 19 | 0.5 | 1140 | 764 | 642 | 352 | 290 | 185 | 4.3 | - | - | - |  |  | 21
05.07.25 | 7.59 | - | 19 | 0.5 | 1110 | 744 | 653 | 339 | 314 | 203 | 4.5 | - | - | - |  |  | 19
07.07.25 | 7.9 | - | 18 | Nil | 1110 | 744 | 670 | 348 | 322 | 177 | 4.5 | - | - | - |  |  | 21
08.07.25 | 7.93 | - | 22 | 0.2 | 1123 | 753 | 661 | 346 | 315 | 164 | 4.4 | - | - | - |  |  | 20
09.07.25 | 8.03 | - | 19 | 0.2 | 1167 | 782 | 674 | 348 | 326 | 174 | 4.2 | - | - | - |  |  | 19
10.07.25 | 7.67 | - | 19 | 0.2 | 1223 | 820 | 676 | 352 | 324 | 189 | 4 | - | - | - |  |  | 20
11.07.25 | 7.86 | - | 17 | 0.1 | 1201 | 805 | 666 | 345 | 321 | 182 | 4.2 | - | - | - |  |  | 18
12.07.25 | 6.47 | - | 15 | 0.4 | 1252 | 839 | 653 | 343 | 310 | 182 | 4.5 | - | - | - |  |  | 20
14.07.25 | 7.98 | - | 19 | 0.1 | 1263 | 846 | 640 | 337 | 303 | 174 | 4.7 | - | - | - |  |  | 18
15.07.25 | 8.14 | - | 20 | 0.1 | 1312 | 879 | 636 | 335 | 301 | 160 | 4.5 | - | - | - |  |  | 20
16.07.25 | 7.98 | - | 19 | 0.4 | 1313 | 880 | 704 | 373 | 331 | 169 | 4.4 | - | - | - |  |  | 18
17.07.25 | 7.68 | - | 17 | 0.5 | 1410 | 945 | 717 | 348 | 369 | 174 | 4.6 | - | - | - |  |  | 16
18.07.25 | 8.11 | - | 22 | Nil | 1461 | 979 | 721 | 367 | 354 | 182 | 4.5 | - | - | - |  |  | 15
19.07.25 | 8.1 | - | 22 | 0.5 | 1365 | 915 | 713 | 363 | 350 | 167 | 4.4 | - | - | - |  |  | 17
27.07.25 | 7.73 | - | 20 | 0.3 | 1360 | 911 | 726 | 376 | 350 | 178 | 4.4 | - | - | - |  |  | 15
22.07.25 | 7.29 | - | 21 | 0.6 | 1423 | 954 | 713 | 367 | 346 | 163 | 4.5 | - | - | - |  |  | 17
23.07.25 | 7.88 | - | 21 | 0.2 | 1428 | 957 | 969 | 384 | 585 | 156 | 4.2 | - | - | - |  |  | 15
24.07.25 | 7.41 | - | 22 | 0.2 | 1460 | 978 | 708 | 376 | 332 | 163 | 4.4 | - | - | - |  |  | 16
25.07.25 | 7.53 | - | 19 | 0.4 | 1497 | 1003 | 726 | 363 | 363 | 142 | 4.5 | - | - | - |  |  | 15
26.07.25 | 7.94 | - | 22 | 0.1 | 1565 | 1049 | 717 | 380 | 337 | 149 | 4.4 | - | - | - |  |  | 16
28.07.25 | STOP
29.07.25 | 8.18 | - | 31 | 0.2 | 1416 | 949 | 736 | 368 | 368 | 142 | 4.1 | - | - | - |  |  | 14
30.07.25 | 7.75 | - | 20 | 0.1 | 2028 | 1359 | 851 | 459 | 392 | 156 | 4.3 | - | - | - |  |  | 16
31.07.25 | 7.98 | - | 22 | 0.4 | 1612 | 1080 | 819 | 460 | 359 | 149 | 4.4 | - | - | - |  |  | -
01.08.25 | 7.56 | - | 20 | NIL | 1643 | 1101 | 857 | 486 | 371 | 142 | 4.2 | - | - | - |  |  | 15
02.08.25 | 7.62 | - | 20 | NIL | 1643 | 1101 | 862 | 481 | 381 | 135 | 4.5 | - | - | - |  |  | 13
04.08.25 | 7.48 | - | 31 | 0.4 | 1188 | 796 | 852 | 476 | 376 | 133 | 4.4 | - | - | - |  |  | 10
05.08.25 | 7.8 | - | 20 | 0.4 | 1137 | 762 | 857 | 483 | 374 | 136 | 4.3 | - | - | - |  |  | 11
06.08.25 | 7.8 | - | 22 | 0.1 | 1298 | 870 | 862 | 476 | 386 | 144 | 4.2 | - | - | - |  |  | 12
07.08.25 | 7.38 | - | 20 | 0.2 | 1232 | 826 | 857 | 481 | 376 | 140 | 4.3 | - | - | - |  |  | 10
08.08.25 | 7.22 | - | 20 | NIL | 1219 | 817 | 852 | 476 | 376 | 151 | 4.1 | - | - | - |  |  | 11
11.08.25 | 8.14 | - | 20 | 0.2 | 1240 | 831 | 819 | 457 | 362 | 144 | 4.3 | - | - | - |  |  | 14
12.08.25 | 7.98 | - | 22 | 0.4 | 1246 | 835 | 814 | 466 | 348 | 151 | 4.2 | - | - | - |  |  | 12
13.08.25 | 7.68 | - | 21 | 0.1 | 1195 | 801 | 738 | 471 | 267 | 158 | 4.1 | - | - | - |  |  | 11
14.08.25 | 8.26 | - | 16 | NIL | 1243 | 833 | 752 | 466 | 286 | 165 | 4.3 | - | - | - |  |  | 10
15.08.25 | 7.81 | - | 19 | NIL | 1194 | 800 | 857 | 438 | 419 | 179 | 4.2 | - | - | - |  |  | 12
18.08.25 | 8.25 | - | 20 | 0.2 | 1280 | 858 | 776 | 443 | 333 | 170 | 4.2 | - | - | - |  |  | 10
19.08.25 | 7.53 | - | 21 | 0.2 | 1322 | 886 | 666 | 395 | 271 | 144 | 4.3 | - | - | - |  |  | 11
20.08.25 | 8.13 | - | 24 | 0.2 | 1361 | 912 | 671 | 400 | 271 | 170 | 4.2 | - | - | - |  |  | 10
21.08.25 | 8.22 | - | 20 | 0.5 | 1286 | 862 | 662 | 409 | 253 | 163 | 4 | - | - | - |  |  | 11
22.08.25 | 7.94 | - | 20 | 0.5 | 1274 | 854 | 676 | 400 | 276 | 156 | 5 | - | - | - |  |  | 12
23.08.25 | 7.92 | - | 22 | 0.5 | 1620 | 1086 | 690 | 390 | 300 | 149 | 5 | - | - | - |  |  | 10
26.08.25 | 8.18 | - | 19 | 0.3 | 1495 | 1002 | 676 | 381 | 295 | 149 | 4.5 | - | - | - |  |  | 12
27.08.25 | 7.99 | - | 21 | 0.5 | 1607 | 1077 | 708 | 426 | 282 | 170 | 4.8 | - | - | - |  |  | 10
28.08.25 | 8.01 | - | 17 | 0.6 | 1537 | 1030 | 685 | 417 | 268 | 156 | 4.5 | - | - | - |  |  | 12
29.08.25 | 8.06 | - | 24 | 0.5 | 1582 | 1060 | 690 | 423 | 267 | 149 | 4.4 | - | - | - |  |  | 10
01.09.25 | 8.4 | 45 | 29 | 0.2 | 1250 | 841 | 510 | 318 | 192 | 319 | 7.2 | 58 | - | 0.3 |  |  | -
02.09.25 | 8.1 |  | 30 | 0.3 | 1418 | 950 | 593 | 370 | 223 | 344 | 7.3 | 52 | Nil | - |  |  | -
03.09.25 | 8.1 | - | 37 | 0.1 | 1603 | 1074 | 632 | 381 | 251 | 336 | 7.3 | 65 | Nil | 0.3 |  |  | 44
04.09.25 | 7.56 | - | 33 | Nil | 1568 | 1051 | 623 | 372 | 251 | 315 | 6.9 | 66 | Nil | 0.4 |  |  | 60
05.09.25 | 7.8 | - | 26 | Nil | 1519 | 1018 | 593 | 367 | 226 | 290 | 7 | 83 | Nil | 0.3 |  |  | 68
06.09.25 | 8.1 | - | 22 | 0.2 | 1380 | 925 | 587 | 360 | 227 | 259 | 6.7 | 85 | Nil | 0.3 |  |  | 57
07.09.25 | 8.02 | - | 22 | Nil | 1403 | 940 | 550 | 336 | 214 | 249 | 6.9 | 90 | Nil | 0.4 |  |  | 60
08.09.25 | 8.51 | - | 20 | 0.3 | 1391 | 932 | 510 | 310 | 200 | 279 | 7 | 105 | 2 | 0.3 |  |  | 66
09.09.25 | 7.9 | - | 21 | 0.4 | 1468 | 984 | 547 | 328 | 219 | 296 | 7 | 87 | Nil | 0.4 |  |  | 69
10.09.25 | 8.2 | - | 19 | 0.4 | 1465 | 982 | 540 | 320 | 220 | 278 | 6.7 | 98 | Nil | 0.4 |  |  | 71
11.09.25 | 7.93 | - | 19 | 0.1 | 1392 | 933 | 590 | 350 | 240 | 286 | 6.5 | 108 | Nil | 0.4 |  |  | 75
12.09.25 | 7.9 | - | 22 | 0.2 | 1678 | 1124 | 570 | 315 | 255 | 289 | 6.3 | 98 | Nil | 0.4 |  |  | 68
13.09.25 | 8.05 | - | 17 | 0.5 | 1667 | 1117 | 565 | 313 | 252 | 280 | 6.8 | 103 | Nil | 0.6 |  |  | 64
14.09.25 | 7.95 | - | 19 | 0.2 | 1589 | 1065 | 578 | 310 | 268 | 268 | 7 | 110 | Nil | 0.6 |  |  | 70
15.09.25 | 8.1 | - | 20 | 0.3 | 1496 | 1002 | 545 | 298 | 247 | 287 | 7.2 | 112 | Nil | 0.6 |  |  | 73
16.09.25 | 7.82 | - | 26 | 0.3 | 1536 | 1029 | 484 | 262 | 222 | 311 | 6.7 | 110 | Nil | 0.6 |  |  | 117
17.09.25 | 7.86 | - | 23 | 0.5 | 1635 | 1096 | 610 | 324 | 286 | 340 | 6.6 | 107 | Nil | 0.5 |  |  | 103
18.09.25 | 8.2 | - | 18 | 0.1 | 1624 | 1088 | 590 | 308 | 282 | 312 | 6.5 | 100 | Nil | 0.6 |  |  | 115
19.09.25 | 8.2 | - | 12 | 0.2 | 1901 | 1274 | 617 | 355 | 262 | 290 | 6.2 | 108 | Nil | 0.8 |  |  | 133
20.09.25 | 8.37 | - | 16 | 0.1 | 1537 | 1030 | 605 | 359 | 246 | 277 | 6.3 | 119 | 1 | 0.7 |  |  | 125
21.09.25 | 8.2 | - | 15 | 0.5 | 1447 | 970 | 580 | 342 | 238 | 268 | 7.7 | 107 | Nil | 0.8 |  |  | 138
22.09.25 | 8.3 | - | 14 | 0.4 | 1522 | 1020 | 576 | 350 | 226 | 283 | 7.1 | 131 | Nil | 0.6 |  |  | 140
23.09.25 | 8.28 | - | 16 | 0.1 | 1492 | 1000 | 670 | 340 | 330 | 274 | 7.2 | 127 | Nil | 0.5 |  |  | 148
24.09.25 | 8.23 | - | 20 | 0.8 | 1302 | 873 | 578 | 318 | 260 | 275 | 7.2 | 102 | Nil | 0.8 |  |  | 140
25.09.25 | 8.2 | - | 25 | 0.4 | 1463 | 980 | 578 | 310 | 268 | 288 | 6.8 | 118 | Nil | 0.6 |  |  | 137
26.09.25 | 8.3 | - | 20 | 0.1 | 1504 | 1008 | 622 | 358 | 264 | 290 | 7 | 126 | Nil | 0.8 |  |  | 141
27.09.25 | 7.9 | - | 34 | 0.1 | 1477 | 990 | 625 | 366 | 259 | 285 | 7.3 | 136 | Nil | 0.7 |  |  | 145
28.09.25 | 8.01 | - | 25 | 0.3 | 1496 | 1002 | 600 | 354 | 246 | 282 | 6.9 | 110 | Nil | 0.8 |  |  | 139
29.09.25 | 8.1 | - | 25 | 0.1 | 1522 | 1020 | 631 | 421 | 210 | 281 | 6.5 | 116 | Nil | 0.8 |  |  | 130
30.09.25 | 7.81 | - | 25 | 0.4 | 1408 | 944 | 637 | 425 | 212 | 280 | 6.8 | 120 | Nil | 0.7 |  |  | 141
01.10.25 | 8.2 | - | 19 | 0.2 | 1338 | 930 | 584 | 396 | 188 | 265 | 6.3 | 110 | - | 0.6 |  |  | 121
02.10.25 | 8.22 | - | 23 | 0.1 | 1478 | 990 | 610 | 394 | 216 | 289 | 7 | 115 | - | 0.7 |  |  | 132
03.10.25 | 8.3 | - | 27 | 0.3 | 1547 | 1037 | 604 | 354 | 250 | 273 | 6.5 | 119 | 2 | 0.7 |  |  | 168
04.10.25 | 7.9 | - | 20 | 0.2 | 1537 | 1030 | 595 | 350 | 245 | 265 | 6.2 | 110 | Nil | 0.6 |  |  | 176
06.10.25 | 7.8 | - | 19 | 0.1 | 1510 | 1012 | 627 | 362 | 265 | 295 | 6.3 | 109 | Nil | 0.6 |  |  | 172
07.10.25 | 7.92 | - | 17 | 0.2 | 1563 | 1047 | 614 | 354 | 260 | 299 | 6.2 |  | Nil | 0.6 |  |  | 120
08.10.25 | 7.41 | - | 21 | 0.4 | 1467 | 983 | 636 | 392 | 244 | 324 | 6.1 | 15 | Nil | 0.5 |  |  | 166
09.10.25 | 7.7 | - | 19 | 0.2 | 1430 | 958 | 610 | 385 | 225 | 308 | 6 | 90 | Nil | 0.5 |  |  | 157
10.10.25 | 7.8 | - | 18 | 0.1 | 1191 | 798 | 520 | 309 | 211 | 294 | 6.1 | 86 | Nil | 0.5 |  |  | 147
11.10.25 | 8.4 | - | 25 | 0.2 | 1179 | 790 | 530 | 338 | 192 | 250 | 6.4 | 100 | 1 | 0.5 |  |  | 140
13.10.25 | 8.33 | - | 25 | 0.2 | 1285 | 861 | 537 | 316 | 221 | 221 | 6.2 | 118 | Nil | 0.6 |  |  | 106
14.10.25 | 8.18 | - | 23 | 0.2 | 1328 | 890 | 540 | 318 | 222 | 250 | 6.5 | 100 | Nil | 0.6 |  |  | 121
15.10.25 | STOP
16.10.25 | STOP
17.10.25 | 8 | - | 30 | Nil | 1399 | 937 | 537 | 318 | 219 | 202 | 6.6 | 90 | Nil | 0.5 |  |  | 130
18.10.25 | STOP
21.10.25 | 7.6 | - | 21 | 0.2 | 1164 | 780 | 524 | 320 | 204 | 230 | 6 | 100 | Nil | 0.5 |  |  | 125
24.10.25 | 8.1 | - | 18 | 0.5 | 1328 | 890 | 548 | 350 | 198 | 254 | 6 | 110 | Nil | 0.6 |  |  | 120
25.10.25 | 8.65 | - | 20 | 0.5 | 1156 | 775 | 524 | 356 | 168 | 247 | 6.3 | 124 | 3 | 0.5 |  |  | 118
27.10.25 | 8.04 | - | 30 | 0.1 | 1243 | 833 | 488 | 278 | 210 | 206 | 6.2 | 98 | Nil | 0.6 |  |  | 124
28.10.25 | 8.2 | - | 33 | 0.1 | 1268 | 850 | 508 | 292 | 216 | 218 | 6.6 | 112 | Nil | 0.7 |  |  | 130
29.10.25 | 8.15 | - | 26 | 0.1 | 1209 | 810 | 508 | 285 | 223 | 210 | 6.4 | 90 | Nil | 0.6 |  |  | 112
30.10.25 | 8.1 | - | 26 | 0.2 | 1328 | 890 | 518 | 310 | 208 | 245 | 6.7 | 98 | Nil | 0.7 |  |  | 128
31.10.25 | 8.35 | - | 32 | 0.6 | 1445 | 968 | 515 | 309 | 206 | 191 | 6.8 | 110 | Nil | 0.7 |  |  | 130
| 6.22 | 17 |  | 0.1 | 764 | 512 | 265 | 153 | 44 | 142 | 5.8 | 15 | 1 | 0.1 | 0 | 0 | 10
MAX. | 8.84 | 28 |  | 1 | 2141 | 1597 | 969 | 524 | 585 | 344 | 10.5 | 136 | 3 | 0.8 | 0 | 0 | 176
AVG. | 7.8321 | 19 |  | 0.3749 | 1358.624 | 911.1407 | 595.7889 | 323.7506 | 272.8518 | 180.6366 | 4.9712 | 96.8 | 0 | 0.54444 |  |  | 44.9027
No. of < Spec | 71 | -- |  | 43 | -- | -- | -- | -- | -- | -- | 141 | -- | -- | -- | -- | -- | --
No. of > Spec | 138 | 146 |  | 46 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 17.8392 | -- |  | 17.4089 | -- | -- | -- | -- | -- | -- | 68.7805 | [5 empty] | --
% > Specs. | 34.6734 | 51.2281 |  | 18.6235 |  | 0 | 0 |  | -- | 0 | 0 | 0 |  | 0 |  |  | 0