## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16 | Unnamed: 17
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2 | COC
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/c m | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm | Based on TH
2013-07-01 | 7.9 | 34 | 0.2 | 2178 | 1525 | 664 | 344 | 320 | 174 | 7.5 | 175 | NIL | 0.2 | 70 | 775 | 95 | 5.53
2013-07-02 | 8 | 29 | 0.2 | 2164 | 1515 | 742 | 371 | 371 | 167 | 7.4 | 180 | NIL | 0.2 | 59 | 843 | 102 | 6.29
2013-07-03 | 7.9 | 30 | 0.2 | 2300 | 1610 | 750 | 375 | 375 | 178 | 7.5 | 170 | NIL | 0.2 | 62 | 886 | 104 | 6.47
2013-07-04 | 7.9 | 24 | 0.2 | 2335 | 1635 | 733 | 362 | 371 | 171 | 7.5 | 173 | NIL | 0.2 | 50 | 899 | 101 | 6.37
2013-07-05 | 7.8 | 20 | 0.2 | 2412 | 1690 | 721 | 354 | 367 | 167 | 7.6 | 165 | NIL | 0.2 | 43 | 921 | 106 | 6.27
2013-07-06 | 7.9 | 23 | 0.2 | 2571 | 1800 | 824 | 383 | 441 | 196 | 7.6 | 170 | NIL | 0.2 | 40 | 939 | 110 | 6.98
2013-07-07 | 7.9 | 21 | 0.2 | 2447 | 1713 | 857 | 396 | 461 | 214 | 7.5 | 170 | NIL | 0.2 | 35 | 928 | 108 | 7.08
2013-07-08 | 7.9 | 18 | 0.2 | 2600 | 1820 | 815 | 375 | 440 | 207 | 7.4 | 160 | NIL | 0.2 | 32 | 910 | 107 | 6.63
2013-07-09 | 7.9 | 15 | 0.2 | 2527 | 1769 | 803 | 367 | 436 | 205 | 7.3 | 160 | NIL | 0.2 | 30 | 924 | 105 | 6.53
2013-07-10 | 7.9 | 16 | 0.2 | 2500 | 1750 | 836 | 375 | 461 | 203 | 7.4 | 170 | NIL | 0.2 | 33 | 938 | 108 | 6.97
2013-07-11 | 8 | 15 | 0.3 | 2400 | 1680 | 783 | 412 | 371 | 196 | 7.8 | 175 | NIL | 0.3 | 35 | 910 | 113 | 6.58
2013-07-12 | 7.9 | 17 | 0.3 | 2428 | 1700 | 824 | 494 | 330 | 212 | 8 | 170 | NIL | 0.3 | 38 | 927 | 118 | 6.87
2013-07-13 | 7.9 | 16 | 0.2 | 2462 | 1724 | 840 | 507 | 333 | 215 | 7.6 | 168 | NIL | 0.2 | 35 | 939 | 114 | 6.94
2013-07-14 | 7.9 | 16 | 0.2 | 2500 | 1750 | 836 | 375 | 461 | 203 | 7.4 | 175 | NIL | 0.2 | 36 | 938 | 108 | 6.97
2013-07-15 | 8 | 17 | 0.2 | 2564 | 1795 | 803 | 474 | 329 | 201 | 8 | 180 | NIL | 0.2 | 31 | 912 | 109 | 6.69
2013-07-16 | 8.2 | 16 | 0.3 | 2657 | 1860 | 812 | 478 | 334 | 194 | 7.9 | 195 | NIL | 0.2 | 33 | 919 | 112 | 6.88
2013-07-17 | 7.8 | 16 | 0.2 | 2600 | 1820 | 762 | 461 | 301 | 208 | 8 | 150 | NIL | 0.2 | 30 | 898 | 107 | 6.4
2013-07-18 | 7.9 | 16 | 0.2 | 2500 | 1750 | 783 | 445 | 338 | 191 | 7.5 | 165 | NIL | 0.2 | 34 | 904 | 109 | 6.69
2013-07-19 | 7.8 | 16 | 0.2 | 2414 | 1690 | 776 | 424 | 352 | 198 | 7 | 155 | NIL | 0.3 | 36 | 921 | 113 | 6.58
2013-07-20 | 7.9 | 14 | 0.2 | 2357 | 1650 | 750 | 411 | 339 | 194 | 7.6 | 165 | NIL | 0.2 | 30 | 933 | 110 | 6.3
2013-07-21 | 8 | 17 | 0.2 | 2564 | 1795 | 803 | 474 | 329 | 201 | 8 | 175 | NIL | 0.2 | 34 | 912 | 109 | 6.98
2013-07-22 | 7.9 | 17 | 0.3 | 2428 | 1700 | 824 | 494 | 330 | 212 | 8 | 180 | NIL | 0.3 | 38 | 927 | 118 | 7.36
2013-07-23 | 7.7 | 15 | 0.2 | 2328 | 1630 | 721 | 440 | 281 | 191 | 7 | 140 | NIL | 0.2 | 33 | 927 | 107 | 6.55
2013-07-24 | 7.8 | 13 | 0.2 | 2371 | 1660 | 742 | 454 | 288 | 198 | 7.9 | 150 | NIL | 0.2 | 29 | 910 | 111 | 7
2013-07-25 | 7.8 | 16 | 0.2 | 2400 | 1680 | 763 | 577 | 186 | 191 | 7.6 | 160 | NIL | 0.2 | 27 | 916 | 115 | 7.06
2013-07-26 | 7.6 | 18 | 0.1 | 2400 | 1680 | 772 | 580 | 192 | 194 | 7 | 140 | NIL | 0.1 | 25 | 929 | 120 | 7.21
2013-07-27 | 7.9 | 16 | 0.2 | 2331 | 1632 | 755 | 572 | 183 | 188 | 7.5 | 170 | NIL | 0.3 | 23 | 902 | 116 | 7.12
2013-07-28 | 7.9 | 17 | 0.3 | 2511 | 1700 | 824 | 494 | 330 | 212 | 8 | 165 | NIL | 0.3 | 21 | 927 | 118 | 7.7
2013-07-29 | 8.1 | 16 | 0.2 | 2357 | 1650 | 763 | 474 | 289 | 191 | 8 | 185 | NIL | 0.3 | 24 | 928 | 114 | 7.06
2013-07-30 | 8 | 16 | 0.3 | 2271 | 1590 | 750 | 466 | 284 | 181 | 7.9 | 190 | NIL | 0.2 | 26 | 932 | 112 | 6.88
2013-07-31 | 8 | 15 | 0.2 | 2357 | 1650 | 763 | 487 | 276 | 181 | 7.2 | 188 | NIL | 0.2 | 28 | 921 | 109 | 7.2
MIN. | 7.6 | 13 | 0.1 | 2164 | 1515 | 664 | 344 | 183 | 167 | 7 | 140 | 0 | 0.1 | 21 | 775 | 95 | 5.5
MAX. | 8.2 | 34 | 0.3 | 2657 | 1860 | 857 | 580 | 461 | 215 | 8 | 195 | 0 | 0.3 | 70 | 939 | 120 | 7.7
AVG. | 7.9 | 18.2 | 0.2 | 2427 | 1697 | 780 | 442 | 339 | 195 | 7.6 | 169 | #DIV/0! | 0.2 | 35.5 | 913 | 110 | 6.8
CWT Monthly Report - JULY-2013