## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
2013-05-01 | 7.92 | 20 | 0.2 | 2430 | 1640 | 907 | 544 | 363 | 132 | 7.3 | 160 | NIL | 0.2 | 35 | 923 | 110
2013-05-02 | 7.95 | 19 | 0.2 | 2380 | 1666 | 929 | 582 | 347 | 146 | 7.3 | 165 | NIL | 0.2 | 32 | 936 | 115
2013-05-03 | 7.8 | 18 | 0.2 | 2280 | 1590 | 877 | 535 | 342 | 139 | 7.2 | 150 | NIL | 0.2 | 30 | 908 | 108
2013-05-04 | 8 | 21 | 0.2 | 2382 | 1668 | 942 | 599 | 343 | 150 | 7.2 | 180 | NIL | 0.2 | 36 | 915 | 116
2013-05-05 | 7.9 | 22 | 0.2 | 2368 | 1658 | 959 | 600 | 359 | 160 | 7.3 | 160 | NIL | 0.2 | 38 | 920 | 118
2013-05-06 | 7.98 | 21 | 0.2 | 2382 | 1668 | 942 | 599 | 343 | 160 | 7.2 | 180 | NIL | 0.2 | 36 | 920 | 110
2013-05-07 | 8.09 | 20 | 0.2 | 2142 | 1500 | 963 | 514 | 449 | 153 | 7.1 | 190 | NIL | 0.2 | 35 | 904 | 104
2013-05-08 | 8.02 | 18 | 0.2 | 2207 | 1545 | 835 | 471 | 364 | 139 | 7.2 | 185 | NIL | 0.2 | 30 | 897 | 99
2013-05-09 | 8.24 | 20 | 0.2 | 2138 | 1497 | 770 | 458 | 312 | 132 | 7.3 | 200 | NIL | 0.2 | 32 | 915 | 96
2013-05-10 | 7.9 | 20 | 0.2 | 2014 | 1410 | 707 | 437 | 270 | 125 | 7.3 | 180 | NIL | 0.2 | 34 | 902 | 93
2013-05-11 | 7.85 | 24 | 0.2 | 2187 | 1531 | 736 | 458 | 278 | 125 | 7.3 | 170 | NIL | 0.2 | 38 | 960 | 96
2013-05-12 | 7.94 | 24 | 0.2 | 2182 | 1528 | 790 | 474 | 316 | 128 | 7.3 | 175 | NIL | 0.2 | 38 | 962 | 95
2013-05-13 | 7.9 | 24 | 0.2 | 2114 | 1480 | 795 | 480 | 315 | 130 | 7.4 | 170 | NIL | 0.2 | 40 | 964 | 96
2013-05-14 | 7.74 | 23 | 0.2 | 2151 | 1506 | 728 | 470 | 258 | 121 | 7.3 | 150 | NIL | 0.2 | 38 | 960 | 96
2013-05-15 | 7.9 | 20 | 0.2 | 2300 | 1610 | 728 | 470 | 258 | 128 | 7.4 | 170 | NIL | 0.2 | 35 | 964 | 95
2013-05-16 | 8.05 | 21 | 0.2 | 2328 | 1630 | 757 | 453 | 304 | 132 | 7.3 | 190 | NIL | 0.2 | 32 | 923 | 98
2013-05-17 | 7.66 | 20 | 0.2 | 2685 | 1880 | 807 | 478 | 329 | 142 | 7.1 | 130 | NIL | 0.2 | 30 | 904 | 102
2013-05-18 | 7.68 | 20 | 0.2 | 2471 | 1730 | 815 | 482 | 333 | 142 | 7.3 | 135 | NIL | 0.2 | 32 | 911 | 105
2013-05-19 | 7.8 | 20 | 0.2 | 2577 | 1804 | 861 | 512 | 349 | 168 | 7.3 | 150 | NIL | 0.2 | 30 | 909 | 102
2013-05-20 | 7.98 | 18 | 0.2 | 2485 | 1740 | 790 | 457 | 333 | 153 | 7.3 | 170 | NIL | 0.2 | 28 | 896 | 112
2013-05-21 | 8.26 | 18 | 0.2 | 2271 | 1590 | 803 | 465 | 338 | 157 | 7.4 | 195 | NIL | 0.2 | 26 | 910 | 114
2013-05-22 | 7.98 | 200 | 0.2 | 2405 | 1684 | 865 | 494 | 371 | 160 | 7.3 | 175 | NIL | 0.2 | 316 | 928 | 118
2013-05-23 | 7.95 | 200 | 0.2 | 3842 | 2690 | 783 | 453 | 330 | 171 | 7.5 | 180 | NIL | 0.2 | 310 | 956 | 123
2013-05-24 | 7.9 | 176 | 0.2 | 3282 | 2298 | 700 | 412 | 288 | 153 | 7.5 | 175 | NIL | 0.2 | 290 | 932 | 111
2013-05-25 | 8 | 180 | 0.2 | 2840 | 1988 | 659 | 371 | 288 | 142 | 7.5 | 180 | NIL | 0.2 | 300 | 908 | 105
2013-05-26 | 8.11 | 116 | 0.2 | 2774 | 1942 | 700 | 412 | 288 | 146 | 7.3 | 190 | NIL | 0.2 | 193 | 900 | 110
2013-05-27 | 7.96 | 94 | 0.2 | 2708 | 1896 | 679 | 424 | 255 | 139 | 7.6 | 180 | NIL | 0.2 | 118 | 891 | 103
2013-05-28 | 8.05 | 89 | 0.2 | 2785 | 1950 | 659 | 416 | 243 | 132 | 7.5 | 190 | NIL | 0.2 | 110 | 910 | 107
2013-05-29 | 8.12 | 83 | 0.2 | 2705 | 1894 | 638 | 403 | 235 | 128 | 7.5 | 195 | NIL | 0.2 | 102 | 902 | 104
2013-05-30 | 8.07 | 52 | 0.2 | 2388 | 1672 | 622 | 391 | 231 | 121 | 7.6 | 180 | NIL | 0.3 | 90 | 889 | 102
2013-05-31 | 8.05 | 50 | 0.2 | 2410 | 1700 | 638 | 400 | 238 | 125 | 7.5 | 185 | NIL | 0.2 | 87 | 911 | 105
MIN. | 7.66 | 18 | 0.2 | 2014 | 1410 | 622 | 371 | 231 | 121 | 7.1 | 130 | 0 | 0.2 | 26 | 889 | 93
MAX. | 8.26 | 200 | 0.2 | 3842 | 2690 | 963 | 600 | 449 | 171 | 7.6 | 200 | 0 | 0.3 | 316 | 964 | 123
AVG. | 7.9597 | 53.9032 | 0.2 | 2471.3871 | 1728.5484 | 786.5806 | 474.6452 | 311.9355 | 141.2581 | 7.3419 | 173.7097 |  | 0.20323 | 84.5484 | 920.3226 | 105.4194
No. of < Spec | 0 | -- | 0 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 10 | 18 | 0 | -- | 2 | 0 | -- | -- | 0 | 31 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- | 0 | -- | -- | -- | -- | -- | -- | 0 | [5 empty] | --
% > Specs. | 32.2581 | 58.0645 | 0 |  | 6.4516 | 0 |  | -- | 0 | 100 | 0 |  | 0 |  | 0 | 0