## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | Total PO4 | T. Alk. | Total Iron | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 4.0 - 6.0 ppm | Max. 200 ppm | Max. 2 ppm | Max. 1000 ppm | 180 ppm
01.08.16 | 7.28 | 11 | 0 | 1320 | 980 | 640 | 340 | 220 | 4.2 | 102 | 0.2 | 978 | 148
02.08.16 | 7.32 | 11 | 0 | 1342 | 988 | 652 | 336 | 226 | 4.1 | 104 | 0.2 | 980 | 149
03.08.16 | 7.35 | 12 | 0 | 1363 | 995 | 664 | 331 | 233 | 4.2 | 100 | 0.2 | 984 | 150
04.08.16 | 7.74 | 12 | 0 | 1357 | 974 | 655 | 319 | 218 | 4.2 | 102 | 0.2 | 970 | 150
05.08.16 | 7.33 | 12 | 0 | 1312 | 995 | 668 | 327 | 233 | 4.1 | 100 | 0.2 | 975 | 149
06.08.16 | 7.3 | 11 | 1 | 1380 | 1016 | 680 | 336 | 272 | 4.1 | 100 | 0.2 | 962 | 149
07.08.16 | 7.54 | 11 | 0.5 | 1410 | 990 | 662 | 328 | 278 | 4.1 | 102 | 0.2 | 960 | 148
08.08.16 | 7.62 | 12 | 0.2 | 1590 | 966 | 643 | 323 | 288 | 4.2 | 100 | 0.2 | 963 | 148
09.08.16 | 7.2 | 12 | 0.2 | 1690 | 970 | 655 | 315 | 280 | 4.1 | 102 | 0.2 | 955 | 146
10.08.16 | 7.32 | 13 | 0.2 | 1630 | 949 | 651 | 298 | 288 | 4.1 | 102 | 0.2 | 950 | 149
11.08.16 | 7.12 | 12 | 0.2 | 1550 | 999 | 655 | 344 | 280 | 4.2 | 103 | 0.2 | 957 | 151
12.08.16 | 7.6 | 12 | 0.2 | 1530 | 982 | 642 | 340 | 292 | 4.1 | 100 | 0.2 | 953 | 149
13.08.16 | 7.7 | 11 | 0.4 | 1680 | 1029 | 693 | 336 | 272 | 4.1 | 103 | 0.2 | 952 | 150
14.08.16 | 7.52 | 12 | 0.2 | 1620 | 1032 | 698 | 334 | 284 | 4.2 | 105 | 0.2 | 948 | 148
15.08.16 | 7.48 | 11 | 0.2 | 1580 | 1048 | 712 | 336 | 296 | 4.1 | 104 | 0.2 | 956 | 150
16.08.16 | 7.24 | 12 | 0.2 | 1546 | 1058 | 731 | 327 | 311 | 4.2 | 102 | 0.2 | 952 | 152
17.08.16 | 7.45 | 11 | 0.6 | 1818 | 1067 | 731 | 336 | 319 | 4.1 | 102 | 0.2 | 951 | 150
18.08.16 | 7.46 | 11 | 0.2 | 1560 | 995 | 685 | 310 | 303 | 4.1 | 105 | 0.2 | 960 | 149
19.08.16 | 7.32 | 11 | 0.1 | 1680 | 1040 | 710 | 330 | 308 | 4.2 | 102 | 0.2 | 963 | 148
20.08.16 | 7.51 | 11 | 0.1 | 1810 | 1100 | 785 | 315 | 327 | 4.1 | 107 | 0.2 | 955 | 152
21.08.16 | 7.38 | 11 | 0.1 | 1570 | 1000 | 655 | 345 | 320 | 4.1 | 110 | 0.2 | 986 | 148
22.08.16 | 7.3 | 11 | 0.1 | 1620 | 1058 | 733 | 325 | 327 | 4.2 | 110 | 0.2 | 939 | 150
23.08.16 | 7.24 | 12 | 0.2 | 1580 | 1020 | 715 | 305 | 311 | 4.2 | 100 | 0.2 | 965 | 147
24.08.16 | 7.33 | 12 | 0.2 | 1610 | 1071 | 748 | 323 | 303 | 4.2 | 100 | 0.2 | 960 | 150
25.08.16 | 7.38 | 11 | 0.2 | 1592 | 1080 | 750 | 330 | 312 | 4.2 | 102 | 0.2 | 957 | 152
26.08.16 | 7.26 | 12 | 0.1 | 1650 | 1050 | 721 | 329 | 285 | 4.2 | 100 | 0.25 | 959 | 152
27.08.16 | 7.68 | 12 | 0.1 | 1638 | 1079 | 756 | 323 | 316 | 4.1 | 104 | 0.25 | 968 | 150
28.08.16 | 7.96 | 12 | 0.1 | 1640 | 1080 | 756 | 323 | 316 | 4.2 | 105 | 0.25 | 963 | 148
29.08.16 | 7.46 | 13 | 0.2 | 1668 | 1108 | 798 | 310 | 318 | 4.1 | 105 | 0.2 | 972 | 150
30.08.16 | 7.8 | 12 | 0.1 | 1650 | 1125 | 790 | 335 | 323 | 4.1 | 103 | 0.2 | 970 | 146
31.08.16 | 7.78 | 13 | 0.5 | 1605 | 1134 | 806 | 328 | 331 | 4.2 | 100 | 0.2 | 972 | 151
MIN. | 7.12 | 11 | 0 | 1312 | 949 | 640 | 298 | 218 | 4.1 | 100 | 0.2 | 939 | 146
MAX. | 7.96 | 13 | 1 | 1818 | 1134 | 806 | 345 | 331 | 4.2 | 110 | 0.25 | 986 | 152
AVG. | 7.4506 | 11.6774 | 0.20645 | 1567.4516 | 1031.5484 | 704.5161 | 327 | 290 | 4.1484 | 102.7742 | 0.20484 | 962.4194 | 149.3226
No. of < Spec | 20 | -- | 13 | -- | -- | -- | -- | -- | 0 | -- | -- | -- | --
No. of > Spec | 0 | 0 | 2 | 0 | 0 | -- | -- | 0 | 0 | 0 | 0 | 0 | 0
% < Specs. | 64.5161 | -- | 41.9355 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 0 | 0 | 6.4516 | 0 | 0 | 0 | -- | 0 | 0 | 0 | 0 | 0 | 0