## Sheet1
CIRCULATING WATER ANALYSIS FOR COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14
DATE | pH | Turbidity | FRC | TDS | TH | CaH | MgH | Cl | ORTHO PO4 | Total PO4 | Total alk | Sulphate | SiO2 | IRON
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | Max. 250 ppm | Max. 1000 ppm | 180 ppm | 3.0 ppm
01.07.16 | 8.7 | 22 | 0 | 817 | 470 | 248 | 222 | 94 | - | 4 | 320 | - | - | 1.2
02.07.16 | 8.67 | 27 | 0 | 885 | 553 | 282 | 271 | 100 | - | 4 | 340 | - | - | 1.2
02.07.16 | 8.3 | 27 | 0 | 893 | 556 | 284 | 272 | 100 | - | 4 | 320 | - | - | 1.2
03.07.16 | 8.7 | 26 | 0 | 890 | 552 | 282 | 270 | 100 | - | 4 | 330 | - | - | 1.2
04.07.16 | 8.76 | 26 | 0 | 890 | 562 | 290 | 272 | 101 | - | 4 | 330 | - | - | 1.3
04.07.16 | 8.24 | 25 | 0 | 886 | 557 | 286 | 271 | 101 | - | 4 | 320 | - | - | 1.3
05.07.16 | 8.79 | 22 | 0 | 923 | 550 | 280 | 270 | 108 | - | 4 | 320 | - | - | 1.3
05.07.16 | 8.02 | 22 | 0 | 940 | 554 | 294 | 260 | 108 | - | 4 | 320 | - | - | 1.3
06.07.16 | 8.7 | 20 | 0 | 910 | 533 | 290 | 243 | 101 | - | 4 | 280 | - | - | 1.3
06.07.16 | 8.08 | 20 | 0 | 931 | 550 | 298 | 252 | 101 | - | 4 | 280 | - | - | 1.3
07.07.16 | 8.68 | 20 | 0 | 936 | 590 | 320 | 270 | 102 | - | 4 | 340 | - | - | 1.3
08.07.16 | 8.72 | 21 | 0 | 942 | 605 | 328 | 277 | 108 | - | 4 | 360 | - | - | 1.3
08.07.16 | 8.03 | 21 | 0 | 916 | 600 | 325 | 275 | 108 | - | 4 | 320 | - | - | 1.3
09.07.16 | 8.73 | 20 | 0 | 844 | 546 | 307 | 239 | 101 | - | 4 | 320 | - | - | 1.3
09.07.16 | 8.01 | 20 | 0 | 842 | 540 | 300 | 240 | 101 | - | 4 | 320 | - | - | 1.3
10.07.16 | 8.72 | 20 | 0 | 880 | 590 | 320 | 270 | 102 | - | 4 | 350 | - | - | 1.3
11.07.16 | 8.68 | 21 | 0 | 980 | 647 | 344 | 303 | 115 | - | 4 | 280 | - | - | 1.3
11.07.16 | 8.02 | 21 | 0 | 970 | 638 | 340 | 298 | 115 | - | 4 | 280 | - | - | 1.3
12.07.16 | 8.65 | 28 | 0 | 885 | 588 | 323 | 265 | 108 | 6 | 10 | 360 | - | - | 1.2
12.07.16 | 7.83 | 28 | 0 | 911 | 601 | 332 | 269 | 108 | 6 | 10 | 240 | - | - | 1.2
13.07.16 | 8.69 | 29 | 0 | 897 | 601 | 332 | 269 | 108 | 6.4 | 10.4 | 320 | - | - | 1.3
13.07.16 | 8.1 | 30 | 0 | 951 | 613 | 349 | 264 | 108 | 6.4 | 10.4 | 280 | - | - | 1.3
15.07.16 | 8.7 | 28 | 0 | 1020 | 706 | 399 | 307 | 122 | 6.5 | 10.5 | 320 | - | - | 1.2
15.07.16 | 7.74 | 28 | 0 | 1040 | 714 | 400 | 314 | 122 | 6.5 | 10.5 | 300 | - | - | 1.2
16.07.16 | 8.72 | 29 | 0 | 1053 | 716 | 405 | 311 | 108 | 6.5 | 10.5 | 360 | - | - | 1.2
MIN. | 7.74 | 20 | 0 | 817 | 470 | 248 | 222 | 94 | 6 | 4 | 240 | 0 | 0 | 1.2
MAX. | 8.79 | 30 | 0 | 1053 | 716 | 405 | 314 | 122 | 6.5 | 10.5 | 360 | 0 | 0 | 1.3
AVG. | 8.4392 | 24.04 | 0 | 921.28 | 589.28 | 318.32 | 270.96 | 106 | 0 | 5.772 | 316.4 | 0 | 0 | 1.264
No. of < Spec | 0 | -- | 25 | -- | -- |  | -- | -- | 0 | -- | - | -- | --
No. of > Spec | 23 | 19 | 0 | 0 | 0 | -- | -- | 0 | 0 | 0 | - | 0 | 0
% < Specs. | 0 | -- | 100 | -- | -- | -- | -- | -- | 0 | - | - | - | --
% > Specs. | 92 | 76 | 0 | 0 | 0 | - | -- | 0 | 0 | 0 | -