## Sheet1
CIRCULATING WATER ANALYSIS FOR MAIN PLANT COOLING TOWER | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | Unnamed: 7 | Unnamed: 8 | Unnamed: 9 | Unnamed: 10 | Unnamed: 11 | Unnamed: 12 | Unnamed: 13 | Unnamed: 14 | Unnamed: 15 | Unnamed: 16
DATE | pH | Turbidity | FRC | COND | TDS | TH | CaH | MgH | Cl | Ortho PO4 | T. Alk. | P. Alk. | Total Iron | SS | Sulphate | SiO2
| 7.5-8.0 | Max. 20 NTU | 0.2 - 0.5 ppm | umho/cm | Max. 2100 ppm | Max. 1200 ppm | ppm | ppm | Max. 500 ppm | 6.0 - 8.0 ppm | Max. 200 ppm | 0 ppm | Max. 2 ppm | ppm | Max. 1000 ppm | 180 ppm
01.10.14 | 7.95 | 20 | 0.1 | 2471 | 1730 | 882 | 538 | 344 | 145 | 7.5 | 150 | NIL | 0.2 | 43 | 864 | 106
02.10.14 | 7.93 | 20 | 0.2 | 2542 | 1780 | 924 | 564 | 360 | 142 | 7.7 | 145 | NIL | 0.2 | 48 | 912 | 105
03.10.14 | 7.95 | 20 | 0.2 | 2550 | 1785 | 928 | 559 | 369 | 152 | 7.7 | 150 | NIL | 0.2 | 53 | 908 | 105
04.10.14 | 7.9 | 24 | 0.1 | 2642 | 1850 | 882 | 538 | 344 | 152 | 8 | 140 | NIL | 0.2 | 49 | 873 | 101
05.10.14 | 7.98 | 24 | 0.1 | 2528 | 1770 | 890 | 546 | 344 | 145 | 7.9 | 160 | NIL | 0.2 | 55 | 878 | 95
06.10.14 | 7.97 | 24 | 0.1 | 2457 | 1720 | 827 | 505 | 322 | 161 | 7.6 | 160 | NIL | 0.2 | 50 | 809 | 82
07.10.14 | 7.8 | 25 | 0.1 | 2285 | 1600 | 693 | 423 | 270 | 126 | 7.5 | 140 | NIL | 0.2 | 54 | 622 | 97
08.10.14 | 7.99 | 18 | 0.1 | 2185 | 1530 | 777 | 474 | 303 | 103 | 7.9 | 155 | NIL | 0.2 | 43 | 762 | 92
09.10.14 | 7.81 | 20 | 0.1 | 2050 | 1435 | 672 | 410 | 262 | 113 | 7.5 | 145 | NIL | 0.2 | 41 | 689 | 89
10.10.14 | 7.86 | 18 | 0.1 | 2157 | 1510 | 693 | 422 | 271 | 126 | 7.2 | 150 | NIL | 0.2 | 37 | 674 | 99
11.10.14 | 7.92 | 19 | 0.1 | 2260 | 1580 | 756 | 461 | 295 | 139 | 7.9 | 155 | NIL | 0.1 | 39 | 721 | 98
12.10.14 | 7.85 | 20 | 0.1 | 1935 | 1355 | 764 | 466 | 298 | 145 | 8 | 135 | NIL | 0.1 | 43 | 742 | 97
13.10.14 | 7.86 | 24 | 0.1 | 1900 | 1330 | 756 | 461 | 295 | 139 | 7.8 | 138 | NIL | 0.1 | 51 | 772 | 87
14.10.14 | 7.69 | 22 | 0.1 | 1885 | 1320 | 790 | 482 | 308 | 126 | 7.7 | 110 | NIL | 0.2 | 47 | 822 | 92
15.10.14 | 7.97 | 20 | 0.2 | 1971 | 1380 | 810 | 494 | 316 | 129 | 7.8 | 140 | NIL | 0.2 | 43 | 833 | 101
16.10.14 | 7.9 | 19 | 0.1 | 2000 | 1400 | 819 | 500 | 319 | 129 | 7.5 | 135 | NIL | 0.1 | 53 | 797 | 105
17.10.14 | 7.95 | 18 | 0.2 | 2114 | 1480 | 865 | 528 | 337 | 135 | 7.7 | 145 | NIL | 0.2 | 41 | 852 | 102
18.10.14 | 7.89 | 25 | 0.1 | 2197 | 1538 | 903 | 551 | 352 | 135 | 7.9 | 140 | NIL | 0.2 | 48 | 898 | 106
19.10.14 | 7.9 | 26 | 0.1 | 2200 | 1580 | 899 | 546 | 353 | 132 | 8 | 140 | NIL | 0.2 | 52 | 891 | 109
20.10.14 | 7.98 | 19 | 0.1 | 2230 | 1540 | 861 | 525 | 336 | 138 | 7.5 | 150 | NIL | 0.2 | 43 | 821 | 104
21.10.14 | 7.98 | 25 | 0.1 | 2310 | 1670 | 874 | 533 | 341 | 145 | 7.8 | 150 | NIL | 0.2 | 55 | 854 | 100
22.10.14 | 7.92 | 26 | 0.1 | 2300 | 1640 | 810 | 494 | 316 | 122 | 7.8 | 145 | NIL | 0.2 | 52 | 793 | 104
23.10.14 | 7.85 | 25 | 0.1 | 2170 | 1525 | 815 | 500 | 315 | 126 | 7.8 | 135 | NIL | 0.2 | 54 | 795 | 97
24.10.14 | 7.9 | 24 | 0.1 | 2160 | 1515 | 810 | 494 | 316 | 129 | 7.6 | 140 | NIL | 0.2 | 50 | 793 | 100
25.10.14 | 7.96 | 21 | 0.1 | 2160 | 1490 | 840 | 512 | 328 | 138 | 7.7 | 145 | NIL | 0.2 | 45 | 826 | 97
26.10.14 | 7.92 | 22 | 0.1 | 2150 | 1485 | 815 | 500 | 315 | 126 | 7.6 | 152 | NIL | 0.2 | 49 | 798 | 100
27.10.14 | 7.9 | 24 | 0.1 | 2160 | 1490 | 819 | 500 | 319 | 129 | 7.7 | 150 | NIL | 0.2 | 46 | 810 | 107
28.10.14 | 7.81 | 22 | 0.1 | 2140 | 1469 | 840 | 512 | 328 | 139 | 7.8 | 140 | NIL | 0.2 | 45 | 830 | 102
29.10.14 | 8.17 | 23 | 0.1 | 2282 | 1600 | 890 | 543 | 347 | 155 | 7.9 | 165 | NIL | 0.2 | 41 | 893 | 111
30.10.14 | 7.89 | 25 | 0.1 | 2295 | 1638 | 924 | 564 | 360 | 162 | 7.9 | 130 | NIL | 0.2 | 51 | 992 | 107
31.10.14 | 7.95 | 18 | 0.1 | 2320 | 1650 | 944 | 574 | 262 | 170 | 7.7 | 145 | 0 | 0.1 | 37 | 820 | 82
MIN. | 8.17 | 26 | 0.2 | 2642 | 1850 | 928 | 564 | 369 | 162 | 8 | 165 | 0 | 0.2 | 55 | 992 | 111
MAX. | 7.9117 | 22.0667 | 0.11333 | 2222.8667 | 1557.8333 | 827.6 | 504.8333 | 322.7667 | 136.1 | 7.73 | 144.5 | NIL | 0.18667 | 47.3667 | 817.4667 | 99.9
No. of < Spec | 0 | -- | 26 | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | --
No. of > Spec | 1 | 18 | 0 | -- | 0 | 0 | -- | -- | 0 | 0 | 0 | -- | 0 | -- | 0 | 0
% < Specs. | 0 | -- | 86.6667 | -- | -- | -- | -- | -- | -- | 0 | - | - | - | - | - | --
% > Specs. | 3.3333 | 60 | 0 | - | 0 | 0 | - | -- | 0 | 0 | 0 | - | 0 | - | 0 | 0